## ACM Performance Curves
Appendix 5.7 Equipment Performance Curves
[44 empty] | Linear | CrvLin
| $A$16:$CE$200 | [42 empty] | BiLinear | CrvDblLin
| Black | Compatible with E+ and DOE-2 curve | [41 empty] | Quadratic | CrvQuad
| Red | EnergyPlus only curve | [41 empty] | BiQuadratic | CrvDblQuad
| Blue | DOE-2 only curve | [41 empty] | Cubic | CrvCubic
| Needs review | [42 empty] | BiCubic | CrvDblCubic
[44 empty] | QuadLinear | CrvQuadplLin
[44 empty] | QuintLinear | CrvQuintplLin
[44 empty] | CoolToolsCT | CrvCoolToolsCap
[68 empty] | Max | 1.05
[40 empty] | Curve Library Text (Copy this column from AP17 to bottom and paste into an editor. Perform the search and replace operations described in Library_PerformanceCurves.rule. Then past edited text into the rule file.) | [27 empty] | Min | 0.95
| !! ACM & I/O REF SECTION/PAGE REFERENCES NEED UPDATING !! | [13 empty] | Variables
| ACM Ref | v1.1 | [15 empty] | Independents | [6 empty] | Coefficients | [8 empty] | Boundaries | [10 empty] | 15 |  | 65 | [6 empty] | 80
| Section | Page no. | Building Descriptor | SDD Object | SDD Short Form | Curve Identifier | Curve ID Abv | Unit System (if Applicable) | Relevant To | DOE-2.2 Keyword | E+ Object | E+ Field(s) | Curve Name (generated from fields) | Curve Type | Dependent | Var1 | Var2 | Var3 | Var4 | Var5 | a | b | c | d | e | f | g | h | i | j | Used to solve for MinVar1 | MaxOut | MinOut | MaxVar1 | MinVar1 | MaxVar2 | MinVar2 | Notes | Include |  | Txt Line 1 | Txt Line 2 | Entry Terminator | Object | Spacing |  | Spacing | Coef1 = | Coef2 = | Coef3 = | Coef4 = | Coef5 = | Coef6 = | Spacing | MaxOut = | MinOut = | MaxVar1 = | MinVar1 = | MaxVar2 = | MinVar2 = |  |  | Var1 Nom | Var2 Nom | MaxVar1 | MinVar1 | MaxVar2 | MinVar2 | OutNom | MaxOut | MinOut | Notes | Example Input | Example Input Value | MaxOutVal | MinOutVal | Notes
FANS | [12 empty] | -
| 5.7.3.2 | 5-099 | Fan Part-Flow Power Curve | Fan | Pwr_fPLRCrvRef | AF or BI Riding the Curve | AForBI |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanAForBIPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.1631 | 1.5901 | -0.8817 | 0.1281 | [6 empty] | 0.7 | 1 | 0.7 | 1 | 0.43668 |  |  |  | 1 | CrvCubic "FanAForBIPwrRatio_fCFMRatio" Coef1 = 0.163100 Coef2 = 1.590100 Coef3 = -0.881700 Coef4 = 0.128100 MaxOut = 1.000 MinOut = 0.700 MaxVar1 = 1.000 MinVar1 = 0.437 .. | CrvCubic "FanAForBIPwrRatio_fCFMRatio" Coef1 = 0.163100 Coef2 = 1.590100 Coef3 = -0.881700 Coef4 = 0.128100 | MaxOut = 1.000 MinOut = 0.700 MaxVar1 = 1.000 MinVar1 = 0.437 | .. | CrvCubic |  | "FanAForBIPwrRatio_fCFMRatio" |  | 0.163100 | 1.590100 | -0.881700 | 0.128100 | - | - |  | 1.000 | 0.700 | 1.000 | 0.437 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.9996 |  | 0.1631
|  |  |  | Fan | Pwr_fPLRCrvRef | AF or BI inlet vanes | AForBIVanes |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanAForBIVanesPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.9977 | -0.659 | 0.9547 | -0.2936 | [6 empty] | 0.87098 | 1 | 0.87 | 1 | 0.51 |  |  |  | 1 | CrvCubic "FanAForBIVanesPwrRatio_fCFMRatio" Coef1 = 0.997700 Coef2 = -0.659000 Coef3 = 0.954700 Coef4 = -0.293600 MaxOut = 1.000 MinOut = 0.870 MaxVar1 = 1.000 MinVar1 = 0.510 .. | CrvCubic "FanAForBIVanesPwrRatio_fCFMRatio" Coef1 = 0.997700 Coef2 = -0.659000 Coef3 = 0.954700 Coef4 = -0.293600 | MaxOut = 1.000 MinOut = 0.870 MaxVar1 = 1.000 MinVar1 = 0.510 | .. | CrvCubic |  | "FanAForBIVanesPwrRatio_fCFMRatio" |  | 0.997700 | -0.659000 | 0.954700 | -0.293600 | - | - |  | 1.000 | 0.870 | 1.000 | 0.510 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.9998 |  | 0.9977
|  |  |  | Fan | Pwr_fPLRCrvRef | FC riding the curve | FC |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanFCPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.1224 | 0.612 | 0.5983 | -0.3334 | [6 empty] | 0.5 | 1 | 0.5 | 1 | 0.46203 |  |  |  | 1 | CrvCubic "FanFCPwrRatio_fCFMRatio" Coef1 = 0.122400 Coef2 = 0.612000 Coef3 = 0.598300 Coef4 = -0.333400 MaxOut = 1.000 MinOut = 0.500 MaxVar1 = 1.000 MinVar1 = 0.462 .. | CrvCubic "FanFCPwrRatio_fCFMRatio" Coef1 = 0.122400 Coef2 = 0.612000 Coef3 = 0.598300 Coef4 = -0.333400 | MaxOut = 1.000 MinOut = 0.500 MaxVar1 = 1.000 MinVar1 = 0.462 | .. | CrvCubic |  | "FanFCPwrRatio_fCFMRatio" |  | 0.122400 | 0.612000 | 0.598300 | -0.333400 | - | - |  | 1.000 | 0.500 | 1.000 | 0.462 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.9993 |  | 0.1224
|  |  |  | Fan | Pwr_fPLRCrvRef | FC with inlet vanes | FCVanes |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanFCVanesPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.3038 | -0.7608 | 2.2729 | -0.8169 | [6 empty] | 0.5 | 1 | 0.5 | 1 | 0.60997 |  |  |  | 1 | CrvCubic "FanFCVanesPwrRatio_fCFMRatio" Coef1 = 0.303800 Coef2 = -0.760800 Coef3 = 2.272900 Coef4 = -0.816900 MaxOut = 1.000 MinOut = 0.500 MaxVar1 = 1.000 MinVar1 = 0.610 .. | CrvCubic "FanFCVanesPwrRatio_fCFMRatio" Coef1 = 0.303800 Coef2 = -0.760800 Coef3 = 2.272900 Coef4 = -0.816900 | MaxOut = 1.000 MinOut = 0.500 MaxVar1 = 1.000 MinVar1 = 0.610 | .. | CrvCubic |  | "FanFCVanesPwrRatio_fCFMRatio" |  | 0.303800 | -0.760800 | 2.272900 | -0.816900 | - | - |  | 1.000 | 0.500 | 1.000 | 0.610 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.999 |  | 0.3038
|  |  |  | Fan | Pwr_fPLRCrvRef | Vane-axial with variable pitch blades | VaneAxVp |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanVaneAxVpPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.1639 | -0.4016 | 1.9909 | -0.7541 | [6 empty] | 0.4 | 1 | 0.4 | 1 | 0.53184 |  |  |  | 1 | CrvCubic "FanVaneAxVpPwrRatio_fCFMRatio" Coef1 = 0.163900 Coef2 = -0.401600 Coef3 = 1.990900 Coef4 = -0.754100 MaxOut = 1.000 MinOut = 0.400 MaxVar1 = 1.000 MinVar1 = 0.532 .. | CrvCubic "FanVaneAxVpPwrRatio_fCFMRatio" Coef1 = 0.163900 Coef2 = -0.401600 Coef3 = 1.990900 Coef4 = -0.754100 | MaxOut = 1.000 MinOut = 0.400 MaxVar1 = 1.000 MinVar1 = 0.532 | .. | CrvCubic |  | "FanVaneAxVpPwrRatio_fCFMRatio" |  | 0.163900 | -0.401600 | 1.990900 | -0.754100 | - | - |  | 1.000 | 0.400 | 1.000 | 0.532 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.9991 |  | 0.1639
|  |  |  | Fan | Pwr_fPLRCrvRef | Any fan with VSD | VSD |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanVSDPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.070429 | 0.38533 | -0.46086 | 1.0092 | [6 empty] | 0.1 | 1 | 0.1 | 1 | 0.083566 |  |  |  | 1 | CrvCubic "FanVSDPwrRatio_fCFMRatio" Coef1 = 0.070429 Coef2 = 0.385330 Coef3 = -0.460864 Coef4 = 1.009203 MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.084 .. | CrvCubic "FanVSDPwrRatio_fCFMRatio" Coef1 = 0.070429 Coef2 = 0.385330 Coef3 = -0.460864 Coef4 = 1.009203 | MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.084 | .. | CrvCubic |  | "FanVSDPwrRatio_fCFMRatio" |  | 0.070429 | 0.385330 | -0.460864 | 1.009203 | - | - |  | 1.000 | 0.100 | 1.000 | 0.084 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 1.0041 |  | 0.070429
|  |  |  | Fan | Pwr_fPLRCrvRef | Any fan with VSD (90.1) | VSD901 |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanVSD901PwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.0013 | 0.147 | 0.9506 | -0.0998 | [6 empty] | 0.19983 | 1 | 0.1998 | 1 | 0.393 |  |  |  | 1 | CrvCubic "FanVSD901PwrRatio_fCFMRatio" Coef1 = 0.001300 Coef2 = 0.147000 Coef3 = 0.950600 Coef4 = -0.099800 MaxOut = 1.000 MinOut = 0.200 MaxVar1 = 1.000 MinVar1 = 0.393 .. | CrvCubic "FanVSD901PwrRatio_fCFMRatio" Coef1 = 0.001300 Coef2 = 0.147000 Coef3 = 0.950600 Coef4 = -0.099800 | MaxOut = 1.000 MinOut = 0.200 MaxVar1 = 1.000 MinVar1 = 0.393 | .. | CrvCubic |  | "FanVSD901PwrRatio_fCFMRatio" |  | 0.001300 | 0.147000 | 0.950600 | -0.099800 | - | - |  | 1.000 | 0.200 | 1.000 | 0.393 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.9991 |  | 0.0013
|  |  |  | Fan | Pwr_fPLRCrvRef | VSD with static pressure reset (Good) | VSDGoodSpReset |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanVSDGoodSpResetPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.04076 | 0.088045 | -0.072926 | 0.94374 | [6 empty] | 0.10009 | 1 | 0.1001 | 1 | 0.342 |  |  |  | 1 | CrvCubic "FanVSDGoodSpResetPwrRatio_fCFMRatio" Coef1 = 0.040760 Coef2 = 0.088045 Coef3 = -0.072926 Coef4 = 0.943740 MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.342 .. | CrvCubic "FanVSDGoodSpResetPwrRatio_fCFMRatio" Coef1 = 0.040760 Coef2 = 0.088045 Coef3 = -0.072926 Coef4 = 0.943740 | MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.342 | .. | CrvCubic |  | "FanVSDGoodSpResetPwrRatio_fCFMRatio" |  | 0.040760 | 0.088045 | -0.072926 | 0.943740 | - | - |  | 1.000 | 0.100 | 1.000 | 0.342 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.99962 |  | 0.04076
|  |  |  | Fan | Pwr_fPLRCrvRef | VSD with static pressure reset (Perfect) | VSDPerfSpReset |  | DOE2, E+ | FAN-EIR-FPLR | Fan:VariableVolume | Fan Power Coefficient 1-5 | FanVSDPerfSpResetPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  |  |  |  | 0.027828 | 0.026583 | -0.087069 | 1.0309 | [6 empty] | 0.1 | 1 | 0.1 | 1 | 0.41997 |  |  |  | 1 | CrvCubic "FanVSDPerfSpResetPwrRatio_fCFMRatio" Coef1 = 0.027828 Coef2 = 0.026583 Coef3 = -0.087069 Coef4 = 1.030920 MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.420 .. | CrvCubic "FanVSDPerfSpResetPwrRatio_fCFMRatio" Coef1 = 0.027828 Coef2 = 0.026583 Coef3 = -0.087069 Coef4 = 1.030920 | MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.420 | .. | CrvCubic |  | "FanVSDPerfSpResetPwrRatio_fCFMRatio" |  | 0.027828 | 0.026583 | -0.087069 | 1.030920 | - | - |  | 1.000 | 0.100 | 1.000 | 0.420 | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 0.99826 |  | 0.027828
PUMPS | [12 empty] | -
| 5.8.5 | 5-168 | Pump Part Load Curve | Pump | Pwr_fPLRCrvRef | VSD | VSDNoRst |  | DOE2 | CIRC-PUMP-FPLR | Pump:Variable Speed | Coefficient 1-4 of the Part Load Performance Curve | PumpVSDNoRstPwrRatio_fGPMRatio | Cubic | PwrRatio | GPMRatio |  |  |  |  | 0 | 0.5726 | -0.301 | 0.7347 | [7 empty] | 1 | 0 | 1 | 0 |  |  |  | 0 | [21 empty] | GPMRatio |  | 1 |  |  | 0 |  |  | 1.0063 |  | 0
|  |  |  | Pump | Pwr_fPLRCrvRef | VSD | VSDRst |  | DOE2 | CIRC-PUMP-FPLR | Pump:Variable Speed | Coefficient 1-4 of the Part Load Performance Curve | PumpVSDRstPwrRatio_fGPMRatio | Cubic | PwrRatio | GPMRatio |  |  |  |  | 0 | 0.0205 | 0.4101 | 0.5753 | [7 empty] | 1 | 0 | 1 | 0 |  |  |  | 0 | [21 empty] | GPMRatio |  | 1 |  |  | 0 |  |  | 1.0059 |  | 0
|  |  |  | Pump | Pwr_fPLRCrvRef | VSD | VSDNoRstEP |  | E+ | CIRC-PUMP-FPLR | Pump:Variable Speed | Coefficient 1-4 of the Part Load Performance Curve | PumpVSDNoRstEPPwrRatio_fGPMRatio | Cubic | PwrRatio | GPMRatio |  |  |  |  | 0.103 | -0.04 | 0.767 | 0.1679 | [6 empty] | 0.12702 | 1 | 0.13 | 1 | 0.2 |  |  |  | 1 | CrvCubic "PumpVSDNoRstEPPwrRatio_fGPMRatio" Coef1 = 0.103000 Coef2 = -0.040000 Coef3 = 0.767000 Coef4 = 0.167900 MaxOut = 1.000 MinOut = 0.130 MaxVar1 = 1.000 MinVar1 = 0.200 .. | CrvCubic "PumpVSDNoRstEPPwrRatio_fGPMRatio" Coef1 = 0.103000 Coef2 = -0.040000 Coef3 = 0.767000 Coef4 = 0.167900 | MaxOut = 1.000 MinOut = 0.130 MaxVar1 = 1.000 MinVar1 = 0.200 | .. | CrvCubic |  | "PumpVSDNoRstEPPwrRatio_fGPMRatio" |  | 0.103000 | -0.040000 | 0.767000 | 0.167900 | - | - |  | 1.000 | 0.130 | 1.000 | 0.200 | - | - | GPMRatio |  | 1 |  |  | 0 |  |  | 0.9979 |  | 0.103
|  |  |  | Pump | Pwr_fPLRCrvRef | VSD | VSDRstEP |  | E+ | CIRC-PUMP-FPLR | Pump:Variable Speed | Coefficient 1-4 of the Part Load Performance Curve | PumpVSDRstEPPwrRatio_fGPMRatio | Cubic | PwrRatio | GPMRatio |  |  |  |  | 0.0273 | -0.1317 | 0.6642 | 0.4445 | [6 empty] | 0.031084 | 1 | 0.03 | 1 | 0.2 |  |  |  | 1 | CrvCubic "PumpVSDRstEPPwrRatio_fGPMRatio" Coef1 = 0.027300 Coef2 = -0.131700 Coef3 = 0.664200 Coef4 = 0.444500 MaxOut = 1.000 MinOut = 0.030 MaxVar1 = 1.000 MinVar1 = 0.200 .. | CrvCubic "PumpVSDRstEPPwrRatio_fGPMRatio" Coef1 = 0.027300 Coef2 = -0.131700 Coef3 = 0.664200 Coef4 = 0.444500 | MaxOut = 1.000 MinOut = 0.030 MaxVar1 = 1.000 MinVar1 = 0.200 | .. | CrvCubic |  | "PumpVSDRstEPPwrRatio_fGPMRatio" |  | 0.027300 | -0.131700 | 0.664200 | 0.444500 | - | - |  | 1.000 | 0.030 | 1.000 | 0.200 | - | - | GPMRatio |  | 1 |  |  | 0 |  |  | 1.0043 |  | 0.0273
COOLING COIL | [12 empty] | -
| 5.7.5.1 | 5-112 | Total Cooling Capacity Adjustment Curve | CoilClg | Cap_fTempCrvRef | Air-Source DX (PTAC) | PTAC | IP | DOE2 | COOL-CAP-FT |  |  | CoilClgPTACQRatio_fTwbToadbIP | BiQuadratic | QRatio | Twb | Toadb |  |  |  | 1.1839 | -0.0081087 | 0.000211 | -0.0061435 | 1.6e-06 | -3e-06 | [5 empty] | 1.34 | 0.7 | 77 | 57 | 115 | 75 | If an air-cooled unit employs an evaporative condenser, Toadb is the effective drybulb temperature of the air leaving the evaporative cooling unit. | 0 | [21 empty] | Twb | Toadb | 67 | 95 | 77 | 57 | 115 | 75 | 0.99954 | 1.3415 | 0.70227 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | Cap_fTempCrvRef | Air-Source DX (PTAC) | PTAC | SI | E+ |  | Coil:Cooling:DX:SingleSpeed Coil:Cooling:DX:TwoSpeed | Total Cooling Capacity Function of Temperature Curve Name | CoilClgPTACQRatio_fTwbToadbSI | BiQuadratic | QRatio | Twb | Toadb |  |  |  | 0.94288 | 0.0095382 | 0.00068364 | -0.011002 | 6.48e-06 | -9.72e-06 | [5 empty] | 1.34 | 0.71 | 25 | 13.89 | 46.11 | 23.89 |  | 1 | CrvDblQuad "CoilClgPTACQRatio_fTwbToadbSI" Coef1 = 0.942879 Coef2 = 0.009538 Coef3 = 0.000684 Coef4 = -0.011002 Coef5 = 0.000006 Coef6 = -0.000010 MaxOut = 1.340 MinOut = 0.710 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgPTACQRatio_fTwbToadbSI" Coef1 = 0.942879 Coef2 = 0.009538 Coef3 = 0.000684 Coef4 = -0.011002 Coef5 = 0.000006 Coef6 = -0.000010 | MaxOut = 1.340 MinOut = 0.710 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgPTACQRatio_fTwbToadbSI" |  | 0.942879 | 0.009538 | 0.000684 | -0.011002 | 0.000006 | -0.000010 |  | 1.340 | 0.710 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4444 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0031 | 1.3437 | 0.70749 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | Cap_fTempCrvRef | Air-Source DX (Other) | DX | IP | DOE2 | COOL-CAP-FT |  |  | CoilClgDXQRatio_fTwbToadbIP | BiQuadratic | QRatio | Twb | Toadb |  |  |  | 0.87403 | -0.0011416 | 0.0001711 | -0.002957 | 1.02e-05 | -5.92e-05 | [5 empty] | 1.29 | 0.77 | 77 | 57 | 115 | 75 | If an air-cooled unit employs an evaporative condenser, Toadb is the effective drybulb temperature of the air leaving the evaporative cooling unit. | 0 | [21 empty] | Twb | Toadb | 67 | 95 | 77 | 57 | 115 | 75 | 0.99994 | 1.2943 | 0.77165 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | Cap_fTempCrvRef | Air-Source DX (Other) | DX | SI | E+ |  | Coil:Cooling:DX:SingleSpeed Coil:Cooling:DX:TwoSpeed | Total Cooling Capacity Function of Temperature Curve Name | CoilClgDXQRatio_fTwbToadbSI | BiQuadratic | QRatio | Twb | Toadb |  |  |  | 0.86779 | 0.014245 | 0.00055404 | -0.007569 | 3.24e-05 | -0.00019116 | [5 empty] | 1.29 | 0.77 | 25 | 13.89 | 46.11 | 23.89 |  | 1 | CrvDblQuad "CoilClgDXQRatio_fTwbToadbSI" Coef1 = 0.867790 Coef2 = 0.014245 Coef3 = 0.000554 Coef4 = -0.007569 Coef5 = 0.000032 Coef6 = -0.000191 MaxOut = 1.290 MinOut = 0.770 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXQRatio_fTwbToadbSI" Coef1 = 0.867790 Coef2 = 0.014245 Coef3 = 0.000554 Coef4 = -0.007569 Coef5 = 0.000032 Coef6 = -0.000191 | MaxOut = 1.290 MinOut = 0.770 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXQRatio_fTwbToadbSI" |  | 0.867790 | 0.014245 | 0.000554 | -0.007569 | 0.000032 | -0.000191 |  | 1.290 | 0.770 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4444 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 0.99893 | 1.2937 | 0.76997 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | Cap_fTempCrvRef | Water-Source DX (HP) | WSHP | IP | DOE2 | COOL-CAP-FT |  |  | CoilClgWSHPQRatio_fTwbTcwsIP | BiQuadratic | QRatio | Twb | Tcws |  |  |  | -0.27804 | 0.024831 | -9.5e-06 | -0.0032731 | 7e-06 | -2.72e-05 | [5 empty] | 1.28 | 0.75 | 77 | 57 | 85 | 60 |  | 0 | [21 empty] | Twb | Tcws | 67 | 85 | 77 | 57 | 85 | 60 | 0.96043 | 1.2808 | 0.74702 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | Cap_fTempCrvRef | Water-Source DX (DX Only) | WSDX | IP | DOE2 | COOL-CAP-FT |  |  | CoilClgWSDXQRatio_fTwbTcwsIP | BiQuadratic | QRatio | Twb | Tcws |  |  |  | 0.94526 | -0.0094199 | 0.000227 | 0.0004805 | -4.5e-06 | -5.99e-05 | [5 empty] | 1.3 | 0.86 | 77 | 57 | 85 | 60 |  | 0 | [21 empty] | Twb | Tcws | 67 | 85 | 77 | 57 | 85 | 60 | 1.0003 | 1.3017 | 0.86397 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | Cap_fTempCrvRef | Water-Source DX | WSDX | SI | E+ |  | Coil:Cooling:WaterToAirHeatPump:EquationFit | Total Cooling Capacity Coefficient 1 to 5 | CoilClgWSDXQRatio_fTwbRatioTwtRatioCFMRatioGPMRatioSI | QuadLinear | QRatio | TwbRatio | TwtRatio | CFMRatio | GPMRatio |  | 3.395 | 5.7257 | 1.8131 | 0.11697 | 0.077143 | [12 empty] | DR: Added, from PNNL document | 0
|  |  |  | CoilClg | Cap_fTempCrvRef | Fan Coils | FC | IP | DOE2 | COOL-CAP-FT |  |  | CoilClgFCQRatio_fTwbTdbIP | BiQuadratic | QRatio | Twb | Tdb |  |  |  | 0.50389 | -0.086918 | 0.0016847 | 0.03363 | 0.0002478 | -0.0010297 | [11 empty] | E+ uses the NTU-effectiveness approach to model water coils, so this curve is not used. | 0 | [21 empty] | Twb | Tdb | 67 | 80 |  |  |  |  | 1.0002
|  |  |  | CoilClg | Cap_fTempCrvRef | Other Chilled Water | ChW | IP | DOE2 | COOL-CAP-FT |  |  | CoilClgChWQRatio_fTwbTdbIP | BiQuadratic | QRatio | Twb | Tdb |  |  |  | 2.5883 | -0.23059 | 0.0038359 | 0.10258 | 0.0005984 | -0.0028721 | [11 empty] | E+ uses the NTU-effectiveness approach to model water coils, so this curve is not used. | 0 | [21 empty] | Twb | Tdb | 67 | 80 |  |  |  |  | 1
| E+ IO Ref | IO p. 1334 | NONE | CoilClg | Cap_fFlowCrvRef | Water-Source DX | WSDX | SI | E+ |  | Coil:Cooling:WaterToAirHeatPump:EquationFit | Sensible Cooling Capacity Coefficient 1 to 5 | CoilClgWSDXQRatio_fTdbRatioTwbRatioTwtRatioCFMRatioGPMRatioSI | QuintLinear | QRatio | TdbRatio | TwbRatio | TwtRatio | CFMRatio | GPMRatio | 4.752 | 19.1845 | 22.7462 | 1.1171 | 0.47516 | 0.060557 | [11 empty] | DR: Added, from PNNL document | 0 | [21 empty] | TdbRatio | TwbRatio
| 5.7.5.1 | 5-113 | Coil Bypass Factor Adjustment Curve | CoilClg | BF_fAirFlowCrvRef | Air-Source DX (PTAC) | PTAC |  | DOE2 | COIL-BF-FFLOW |  |  | CoilClgPTACCoilBPF_fCFMRatio | Cubic | CoilBPF | CFMRatio |  |  |  |  | -2.277 | 5.2114 | -1.9344 | 0 | [14 empty] | 0 | [21 empty] | CFMRatio |  | 1 |  |  | 0 |  |  | 1
|  |  |  | CoilClg | BF_fAirFlowCrvRef | Air-Source DX (HP) | HP |  | DOE2 | COIL-BF-FFLOW |  |  | CoilClgHPCoilBPF_fCFMRatio | Cubic | CoilBPF | CFMRatio |  |  |  |  | -0.82816 | 14.3179 | -21.8894 | 9.3997 | [14 empty] | 0 | [21 empty] | CFMRatio |  | 1 |  |  | 0 |  |  | 1
|  |  |  | CoilClg | BF_fAirFlowCrvRef | Air-Source DX (PSZ and other) | DX |  | DOE2 | COIL-BF-FFLOW |  |  | CoilClgDXCoilBPF_fCFMRatio | Cubic | CoilBPF | CFMRatio |  |  |  |  | -0.25423 | 1.2183 | 0.035978 | 0 | [14 empty] | 0 | [21 empty] | CFMRatio |  | 1 |  |  | 0 |  |  | 1
|  |  |  | CoilClg | BF_fTempCrvRef | Air-Source DX (All) | All | IP | DOE2 | COIL-BF-FT |  |  | CoilClgAllCoilBPF_fTwbTdbIP | BiQuadratic | CoilBPF | Twb | Tdb |  |  |  | 1.066 | -0.000517 | 5.67e-05 | -0.012918 | -1.7e-06 | 0.0001503 | [5 empty] | 1.26 | 0.82 | 77 | 57 | 90 | 70 |  | 0 | [21 empty] | Twb | Tdb | 67 | 80 | 77 | 57 | 90 | 70 | 1.0472 | 1.2599 | 0.81539
|  |  |  | CoilClg | BF_fPLRCrvRef | Air-Source DX (PTAC) | PTAC |  | DOE2 | COIL-BF-FPLR |  |  | CoilClgPTACCoilBPF_fQRatio | Linear | CoilBPF | QRatio |  |  |  |  | 0 | 1 | [16 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0
|  |  |  | CoilClg | BF_fPLRCrvRef | Air-Source DX (HP) | HP |  | DOE2 | COIL-BF-FPLR |  |  | CoilClgHPCoilBPF_fQRatio | Linear | CoilBPF | QRatio |  |  |  |  | 0 | 1 | [16 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0
|  |  |  | CoilClg | BF_fPLRCrvRef | Air-Source DX (PSZ and other) | DX |  | DOE2 | COIL-BF-FPLR |  |  | CoilClgDXCoilBPF_fQRatio | Linear | CoilBPF | QRatio |  |  |  |  | 0 | 1 | [16 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0
| E+ IO Ref | IO p. 1241 | NONE | CoilClg | Cap_fFlowCrvRef | Air-Source DX (Single speed) | DXSngl |  | E+ |  | Coil:Cooling:DX:SingleSpeed | Total Cooling Capacity Function of Flow Fraction Curve | CoilClgDXSnglQRatio_fCFMRatio | Quadratic | QRatio | CFMRatio |  |  |  |  | 0.8 | 0.2 | 0 | [9 empty] | 0.8 |  |  |  |  | DR: Added, from CEC Reference E+ models | 1 | CrvQuad "CoilClgDXSnglQRatio_fCFMRatio" Coef1 = 0.800000 Coef2 = 0.200000 Coef3 = 0.000000 MinOut = 0.800 .. | CrvQuad "CoilClgDXSnglQRatio_fCFMRatio" Coef1 = 0.800000 Coef2 = 0.200000 Coef3 = 0.000000 | MinOut = 0.800 | .. | CrvQuad |  | "CoilClgDXSnglQRatio_fCFMRatio" |  | 0.800000 | 0.200000 | 0.000000 | - | - | - |  | - | 0.800 | - | - | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.8
|  |  |  | CoilClg | Cap_fFlowCrvRef | Air-Source DX (Two speed) | DXDbl |  | E+ |  | Coil:Cooling:DX:TwoSpeed | Total Cooling Capacity Function of Flow Fraction Curve | CoilClgDXDblQRatio_fCFMRatio | Cubic | QRatio | CFMRatio |  |  |  |  | 0.47279 | 1.2433 | -1.0387 | 0.32258 | [8 empty] | 0.47 |  |  |  |  | DR: Added, from CEC Reference E+ models | 1 | CrvCubic "CoilClgDXDblQRatio_fCFMRatio" Coef1 = 0.472786 Coef2 = 1.243342 Coef3 = -1.038706 Coef4 = 0.322578 MinOut = 0.470 .. | CrvCubic "CoilClgDXDblQRatio_fCFMRatio" Coef1 = 0.472786 Coef2 = 1.243342 Coef3 = -1.038706 Coef4 = 0.322578 | MinOut = 0.470 | .. | CrvCubic |  | "CoilClgDXDblQRatio_fCFMRatio" |  | 0.472786 | 1.243342 | -1.038706 | 0.322578 | - | - |  | - | 0.470 | - | - | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.47279
| 5.7.5.2 | 5-116 | Direct Expansion Cooling Efficiency Temperature Adjustment Curve | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PTAC) | PTAC | IP | DOE2 | DX-EIR-FT |  |  | CoilClgPTACEIRRatio_fTwbToadbIP | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -0.65505 | 0.038891 | -0.0001925 | 0.0013046 | 0.0001352 | -0.0002247 | [5 empty] | 1.4 | 0.76 | 77 | 57 | 115 | 75 | If an air-cooled unit employs an evaporative condenser, Toadb is the effective drybulb temperature of the air leaving the evaporative cooling unit. | 0 | [21 empty] | Twb | Toadb | 67 | 95 | 77 | 57 | 115 | 75 | 1.0004 | 1.4014 | 0.75893 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PTAC) | PTAC | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgPTACEIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | 0.34143 | 0.03481 | -0.00062532 | 0.004941 | 0.0004374 | -0.000729 | [5 empty] | 1.4 | 0.75 | 25 | 13.89 | 46.11 | 23.89 |  | 1 | CrvDblQuad "CoilClgPTACEIRRatio_fTwbToadbSI" Coef1 = 0.341434 Coef2 = 0.034810 Coef3 = -0.000625 Coef4 = 0.004941 Coef5 = 0.000437 Coef6 = -0.000729 MaxOut = 1.400 MinOut = 0.750 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgPTACEIRRatio_fTwbToadbSI" Coef1 = 0.341434 Coef2 = 0.034810 Coef3 = -0.000625 Coef4 = 0.004941 Coef5 = 0.000437 Coef6 = -0.000729 | MaxOut = 1.400 MinOut = 0.750 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgPTACEIRRatio_fTwbToadbSI" |  | 0.341434 | 0.034810 | -0.000625 | 0.004941 | 0.000437 | -0.000729 |  | 1.400 | 0.750 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4444 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 0.9945 | 1.3953 | 0.75314 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXSEER | IP | DOE2 | DX-EIR-FT |  |  | CoilClgDXSEEREIRRatio_fTwbToadbIP | BiQuadratic | EIRRatio | Twb | Toadb | [16 empty] | 77 | 57 | 115 | 75 | Performance curve map based on ACM equations | 0 | [21 empty] | Twb | Toadb | 67 | 95 | 77 | 57 | 115 | 75 |  | 0 | 0 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXEER11SEER13 | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | 0.68668 | -0.035826 | 0.000781 | 0.025564 | 0.000163 | -0.000559 | [5 empty] | 1.51 | 0.65 | 25 | 13.89 | 46.11 | 23.89 | EER < 13, SEER < 15 | 1 | CrvDblQuad "CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI" Coef1 = 0.686684 Coef2 = -0.035826 Coef3 = 0.000781 Coef4 = 0.025564 Coef5 = 0.000163 Coef6 = -0.000559 MaxOut = 1.510 MinOut = 0.650 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI" Coef1 = 0.686684 Coef2 = -0.035826 Coef3 = 0.000781 Coef4 = 0.025564 Coef5 = 0.000163 Coef6 = -0.000559 | MaxOut = 1.510 MinOut = 0.650 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI" |  | 0.686684 | -0.035826 | 0.000781 | 0.025564 | 0.000163 | -0.000559 |  | 1.510 | 0.650 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0005 | 1.5071 | 0.64903 | Max/MinVar switch to get Max/MinOut | 0.33333 | EIR | 0.50237 | 0.21634 | Smaller value = more eff
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXEER11SEER15 | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEER11SEER15EIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -1.2471 | -0.027513 | 0.000752 | 0.12112 | -0.001013 | -0.000736 | [5 empty] | 1.48 | 0.41 | 25 | 13.89 | 46.11 | 23.89 | EER < 13, SEER >= 15 | 1 | CrvDblQuad "CoilClgDXEER11SEER15EIRRatio_fTwbToadbSI" Coef1 = -1.247121 Coef2 = -0.027513 Coef3 = 0.000752 Coef4 = 0.121123 Coef5 = -0.001013 Coef6 = -0.000736 MaxOut = 1.480 MinOut = 0.410 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEER11SEER15EIRRatio_fTwbToadbSI" Coef1 = -1.247121 Coef2 = -0.027513 Coef3 = 0.000752 Coef4 = 0.121123 Coef5 = -0.001013 Coef6 = -0.000736 | MaxOut = 1.480 MinOut = 0.410 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEER11SEER15EIRRatio_fTwbToadbSI" |  | -1.247121 | -0.027513 | 0.000752 | 0.121123 | -0.001013 | -0.000736 |  | 1.480 | 0.410 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0008 | 1.4757 | 0.41089 | Max/MinVar switch to get Max/MinOut | 0.33333 | EIR | 0.4919 | 0.13696 | Smaller value = more eff
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXEER11SEER17 | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEER11SEER17EIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -2.7249 | -0.02112 | 0.00073 | 0.19413 | -0.001911 | -0.000872 | [5 empty] | 1.45 | 0.23 | 25 | 13.89 | 46.11 | 23.89 | EER < 13, SEER >= 17 | 1 | CrvDblQuad "CoilClgDXEER11SEER17EIRRatio_fTwbToadbSI" Coef1 = -2.724920 Coef2 = -0.021120 Coef3 = 0.000730 Coef4 = 0.194128 Coef5 = -0.001911 Coef6 = -0.000872 MaxOut = 1.450 MinOut = 0.230 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEER11SEER17EIRRatio_fTwbToadbSI" Coef1 = -2.724920 Coef2 = -0.021120 Coef3 = 0.000730 Coef4 = 0.194128 Coef5 = -0.001911 Coef6 = -0.000872 | MaxOut = 1.450 MinOut = 0.230 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEER11SEER17EIRRatio_fTwbToadbSI" |  | -2.724920 | -0.021120 | 0.000730 | 0.194128 | -0.001911 | -0.000872 |  | 1.450 | 0.230 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0015 | 1.4523 | 0.22949 | Max/MinVar switch to get Max/MinOut | 0.33333 | EIR | 0.48411 | 0.076496 | Smaller value = more eff
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXEER13SEER16 | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -0.19999 | -0.035686 | 0.000787 | 0.074834 | -0.000516 | -0.000573 | [5 empty] | 1.44 | 0.55 | 25 | 13.89 | 46.11 | 23.89 | EER >= 13, SEER < 18 | 1 | CrvDblQuad "CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI" Coef1 = -0.199992 Coef2 = -0.035686 Coef3 = 0.000787 Coef4 = 0.074834 Coef5 = -0.000516 Coef6 = -0.000573 MaxOut = 1.440 MinOut = 0.550 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI" Coef1 = -0.199992 Coef2 = -0.035686 Coef3 = 0.000787 Coef4 = 0.074834 Coef5 = -0.000516 Coef6 = -0.000573 | MaxOut = 1.440 MinOut = 0.550 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI" |  | -0.199992 | -0.035686 | 0.000787 | 0.074834 | -0.000516 | -0.000573 |  | 1.440 | 0.550 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0019 | 1.4428 | 0.55076 | Max/MinVar switch to get Max/MinOut | 0.33333 | EIR | 0.48092 | 0.18359 | Smaller value = more eff
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXEER13SEER18 | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -1.7905 | -0.028777 | 0.000763 | 0.15339 | -0.001482 | -0.000721 | [5 empty] | 1.42 | 0.35 | 25 | 13.89 | 46.11 | 23.89 | EER >= 13, SEER >= 18 | 1 | CrvDblQuad "CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI" Coef1 = -1.790474 Coef2 = -0.028777 Coef3 = 0.000763 Coef4 = 0.153391 Coef5 = -0.001482 Coef6 = -0.000721 MaxOut = 1.420 MinOut = 0.350 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI" Coef1 = -1.790474 Coef2 = -0.028777 Coef3 = 0.000763 Coef4 = 0.153391 Coef5 = -0.001482 Coef6 = -0.000721 | MaxOut = 1.420 MinOut = 0.350 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI" |  | -1.790474 | -0.028777 | 0.000763 | 0.153391 | -0.001482 | -0.000721 |  | 1.420 | 0.350 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0021 | 1.4172 | 0.35497 | Max/MinVar switch to get Max/MinOut | 0.33333 | EIR | 0.47241 | 0.11832 | Smaller value = more eff
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (PSZ <65,000) | DXEER13SEER20 | SI | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEER13SEER20EIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -3.0605 | -0.023207 | 0.000744 | 0.21609 | -0.002253 | -0.000839 | [5 empty] | 1.4 | 0.2 | 25 | 13.89 | 46.11 | 23.89 | EER >= 13, SEER >= 20 | 1 | CrvDblQuad "CoilClgDXEER13SEER20EIRRatio_fTwbToadbSI" Coef1 = -3.060538 Coef2 = -0.023207 Coef3 = 0.000744 Coef4 = 0.216093 Coef5 = -0.002253 Coef6 = -0.000839 MaxOut = 1.400 MinOut = 0.200 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEER13SEER20EIRRatio_fTwbToadbSI" Coef1 = -3.060538 Coef2 = -0.023207 Coef3 = 0.000744 Coef4 = 0.216093 Coef5 = -0.002253 Coef6 = -0.000839 | MaxOut = 1.400 MinOut = 0.200 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEER13SEER20EIRRatio_fTwbToadbSI" |  | -3.060538 | -0.023207 | 0.000744 | 0.216093 | -0.002253 | -0.000839 |  | 1.400 | 0.200 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 1.0029 | 1.3972 | 0.1997 | Max/MinVar switch to get Max/MinOut | 0.33333 | EIR | 0.46574 | 0.066566 | Smaller value = more eff
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (Other) | DX | IP | DOE2 | DX-EIR-FT |  |  | CoilClgDXEIRRatio_fTwbToadbIP | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | -1.0639 | 0.030658 | -0.0001269 | 0.015421 | 4.97e-05 | -0.0002096 | [5 empty] | 1.33 | 0.77 | 77 | 57 | 115 | 75 | If an air-cooled unit employs an evaporative condenser, Toadb is the effective drybulb temperature of the air leaving the evaporative cooling unit. | 0 | [21 empty] | Twb | Toadb | 67 | 95 | 77 | 57 | 115 | 75 | 0.99999 | 1.3281 | 0.7701 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Air-Source DX (Other) | DX | SI | E+ |  | Coil:Cooling:DX:SingleSpeed Coil:Cooling:DX:TwoSpeed | Energy Input Ratio Function of Temperature Curve | CoilClgDXEIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb |  |  |  | 0.11671 | 0.028458 | -0.00041148 | 0.021422 | 0.000162 | -0.0006804 | [5 empty] | 1.33 | 0.77 | 25 | 13.89 | 46.11 | 23.89 |  | 1 | CrvDblQuad "CoilClgDXEIRRatio_fTwbToadbSI" Coef1 = 0.116709 Coef2 = 0.028458 Coef3 = -0.000411 Coef4 = 0.021422 Coef5 = 0.000162 Coef6 = -0.000680 MaxOut = 1.330 MinOut = 0.770 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "CoilClgDXEIRRatio_fTwbToadbSI" Coef1 = 0.116709 Coef2 = 0.028458 Coef3 = -0.000411 Coef4 = 0.021422 Coef5 = 0.000162 Coef6 = -0.000680 | MaxOut = 1.330 MinOut = 0.770 MaxVar1 = 25.000 MinVar1 = 13.890 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "CoilClgDXEIRRatio_fTwbToadbSI" |  | 0.116709 | 0.028458 | -0.000411 | 0.021422 | 0.000162 | -0.000680 |  | 1.330 | 0.770 | 25.000 | 13.890 | 46.110 | 23.890 | Twb | Toadb | 19.4444 | 35 | 25 | 13.8889 | 46.1111 | 23.8889 | 0.99965 | 1.3291 | 0.76883 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Water-Source (HP) | WSHP | IP | DOE2 | DX-EIR-FT |  |  | CoilClgWSHPEIRRatio_fTwbTcwsIP | BiQuadratic | EIRRatio | Twb | Tcws |  |  |  | 2.028 | -0.042309 | 0.0003054 | 0.014967 | 2.44e-05 | -0.000164 | [5 empty] | 0.96 | 1.03 | 57 | 77 | 85 | 60 |  | 0 | [21 empty] | Twb | Tcws | 67 | 75 | 57 | 77 | 85 | 60 | 0.99996 | 0.95608 | 1.0337 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Water-Source (Other) | WSDX | IP | DOE2 | DX-EIR-FT |  |  | CoilClgWSDXEIRRatio_fTwbTcwsIP | BiQuadratic | EIRRatio | Twb | Tcws |  |  |  | -1.8395 | 0.075136 | -0.0005686 | 0.004709 | 9.01e-05 | -0.0001218 | [5 empty] | 0.83 | 0.79 | 57 | 77 | 85 | 60 |  | 0 | [21 empty] | Twb | Tcws | 67 | 85 | 57 | 77 | 85 | 60 | 0.9998 | 0.82885 | 0.78626 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilClg | DXEIR_fTempCrvRef | Water-Source DX | WSDX | SI | E+ |  | Coil:Cooling:WaterToAirHeatPump:EquationFit | Cooling Power Consumption Coefficient 1 to 5 | CoilClgWSDXEIRRatio_fTwbRatioTwtRatioCFMRatioGPMRatioSI | QuadLinear | EIRRatio | TwbRatio | TwtRatio | CFMRatio | GPMRatio |  | 7.3945 | 0.82845 | 7.8532 | 0.26946 | 0.29678 | [12 empty] | DR: Added, from PNNL document | 0 | [21 empty] | TwbRatio | TwtRatio
| E+ IO Ref | IO p. 1241 | NONE | CoilClg | DXEIR_fFlowCrvRef | Air-Source DX (Single speed) | DXSngl |  | E+ |  | Coil:Cooling:DX:SingleSpeed | Energy Input Ratio Function of Flow Fraction Curve | CoilClgDXSnglEIRRatio_fCFMRatio | Quadratic | EIRRatio | CFMRatio |  |  |  |  | 1.156 | -0.1816 | 0.0256 | [14 empty] | DR: Added, from CEC Reference E+ models | 1 | CrvQuad "CoilClgDXSnglEIRRatio_fCFMRatio" Coef1 = 1.156000 Coef2 = -0.181600 Coef3 = 0.025600 .. | CrvQuad "CoilClgDXSnglEIRRatio_fCFMRatio" Coef1 = 1.156000 Coef2 = -0.181600 Coef3 = 0.025600 |  | .. | CrvQuad |  | "CoilClgDXSnglEIRRatio_fCFMRatio" |  | 1.156000 | -0.181600 | 0.025600 | - | - | - |  | - | - | - | - | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 1
|  |  |  | CoilClg | DXEIR_fFlowCrvRef | Air-Source DX (Two speed) | DXDbl |  | E+ |  | Coil:Cooling:DX:TwoSpeed | Energy Input Ratio Function of Flow Fraction Curve | CoilClgDXDblEIRRatio_fCFMRatio | Cubic | EIRRatio | CFMRatio |  |  |  |  | 1.0079 | 0.34544 | -0.69229 | 0.3389 | [13 empty] | DR: Added, from CEC Reference E+ models | 1 | CrvCubic "CoilClgDXDblEIRRatio_fCFMRatio" Coef1 = 1.007948 Coef2 = 0.345441 Coef3 = -0.692289 Coef4 = 0.338899 .. | CrvCubic "CoilClgDXDblEIRRatio_fCFMRatio" Coef1 = 1.007948 Coef2 = 0.345441 Coef3 = -0.692289 Coef4 = 0.338899 |  | .. | CrvCubic |  | "CoilClgDXDblEIRRatio_fCFMRatio" |  | 1.007948 | 0.345441 | -0.692289 | 0.338899 | - | - |  | - | - | - | - | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 1
| 5.7.5.2 | 5-119 | Direct-Expansion Part-Load Efficiency Adjustment Curve | CoilClg | DXEIR_fPLRCrvRef | Water-Source DX (HP) | WSHP |  | DOE2 | DX-EIR-FPLR |  |  | CoilClgWSHPEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  |  |  |  | 0.125 | 0.875 | 0 | 0 | [8 empty] | 0.13 | [5 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.125
|  |  |  | CoilClg | DXEIR_fPLRCrvRef | Water-Source DX (DX Only) | WSDX |  | DOE2 | DX-EIR-FPLR |  |  | CoilClgWSDXEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  |  |  |  | 0.20123 | -0.031217 | 1.9505 | -1.1205 | [8 empty] | 0.2 | [5 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.20123
|  |  |  | CoilClg | DXEIR_fPLRCrvRef | Air-Source DX (PTAC) | PTAC |  | DOE2 | DX-EIR-FPLR |  |  | CoilClgPTACEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  |  |  |  | 0.125 | 0.875 | 0 | 0 | [8 empty] | 0.13 | [5 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.125
|  |  |  | CoilClg | DXEIR_fPLRCrvRef | Air-Source DX (SEER) | DXSEER |  | DOE2 | DX-EIR-FPLR |  |  | CoilClgDXSEEREIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  |  |  |  | 0 | 1 | 0 | 0 | [14 empty] | 0 | [23 empty] | 1 |  |  | 0 |  |  | 1 |  | 0
|  |  |  | CoilClg | DXEIR_fPLRCrvRef | Air-Source DX (Other) | DX |  | DOE2 | DX-EIR-FPLR |  |  | CoilClgDXEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  |  |  |  | 0.20123 | -0.031217 | 1.9505 | -1.1205 | [8 empty] | 0.2 | [5 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.20123
| 5.7.5.2 | 5-119 | Direct-Expansion Part-Load Efficiency Adjustment Curve | CoilClg | DXEIR_fPLFCrvRef | Air-Source DX (PTAC) | PTAC |  | E+ |  | Coil:Cooling:DX:SingleSpeed | Part Load Fraction Correlation Curve | CoilClgPTACEIRRatio_fQFrac | Cubic | EIRRatio | QFrac |  |  |  |  | 0.85 | 0.15 | 0 | 0 | [7 empty] | 1 | 0.96 | 1 | 0.7 |  |  |  | 1 | CrvCubic "CoilClgPTACEIRRatio_fQFrac" Coef1 = 0.850000 Coef2 = 0.150000 Coef3 = 0.000000 Coef4 = 0.000000 MaxOut = 1.000 MinOut = 0.960 MaxVar1 = 1.000 MinVar1 = 0.700 .. | CrvCubic "CoilClgPTACEIRRatio_fQFrac" Coef1 = 0.850000 Coef2 = 0.150000 Coef3 = 0.000000 Coef4 = 0.000000 | MaxOut = 1.000 MinOut = 0.960 MaxVar1 = 1.000 MinVar1 = 0.700 | .. | CrvCubic |  | "CoilClgPTACEIRRatio_fQFrac" |  | 0.850000 | 0.150000 | 0.000000 | 0.000000 | - | - |  | 1.000 | 0.960 | 1.000 | 0.700 | - | - | QFrac |  | 1 |  | 1 | 0.7 |  |  | 1 | 1 | 0.955
|  |  |  | CoilClg | DXEIR_fPLFCrvRef | Air-Source DX (SEER) | DXSEER |  | E+ |  | Coil:Cooling:DX:SingleSpeed | Part Load Fraction Correlation Curve | CoilClgDXSEEREIRRatio_fQFrac | Cubic | EIRRatio | QFrac |  |  |  |  | 1 | 0 | 0 | 0 | [7 empty] | 1 | 1 | 1 | 0.7 |  |  |  | 1 | CrvCubic "CoilClgDXSEEREIRRatio_fQFrac" Coef1 = 1.000000 Coef2 = 0.000000 Coef3 = 0.000000 Coef4 = 0.000000 MaxOut = 1.000 MinOut = 1.000 MaxVar1 = 1.000 MinVar1 = 0.700 .. | CrvCubic "CoilClgDXSEEREIRRatio_fQFrac" Coef1 = 1.000000 Coef2 = 0.000000 Coef3 = 0.000000 Coef4 = 0.000000 | MaxOut = 1.000 MinOut = 1.000 MaxVar1 = 1.000 MinVar1 = 0.700 | .. | CrvCubic |  | "CoilClgDXSEEREIRRatio_fQFrac" |  | 1.000000 | 0.000000 | 0.000000 | 0.000000 | - | - |  | 1.000 | 1.000 | 1.000 | 0.700 | - | - | QFrac |  | 1 |  | 1 | 0.7 |  |  | 1 | 1 | 1
|  |  |  | CoilClg | DXEIR_fPLFCrvRef | Air-Source DX (Other) | DX |  | E+ |  | Coil:Cooling:DX:SingleSpeed Coil:Cooling:DX:TwoSpeed | Part Load Fraction Correlation Curve | CoilClgDXEIRRatio_fQFrac | Cubic | EIRRatio | QFrac |  |  |  |  | 0 | 5.1091 | -8.5515 | 4.4744 | [7 empty] | 1 | 0.92 | 1 | 0.7 |  |  |  | 1 | CrvCubic "CoilClgDXEIRRatio_fQFrac" Coef1 = 0.000000 Coef2 = 5.109100 Coef3 = -8.551500 Coef4 = 4.474400 MaxOut = 1.000 MinOut = 0.920 MaxVar1 = 1.000 MinVar1 = 0.700 .. | CrvCubic "CoilClgDXEIRRatio_fQFrac" Coef1 = 0.000000 Coef2 = 5.109100 Coef3 = -8.551500 Coef4 = 4.474400 | MaxOut = 1.000 MinOut = 0.920 MaxVar1 = 1.000 MinVar1 = 0.700 | .. | CrvCubic |  | "CoilClgDXEIRRatio_fQFrac" |  | 0.000000 | 5.109100 | -8.551500 | 4.474400 | - | - |  | 1.000 | 0.920 | 1.000 | 0.700 | - | - | QFrac |  | 1 |  | 1 | 0.7 |  |  | 1.032 | 1 | 0.92085 | Cause E+ warning since Output at 0.99 is > 1.0
HEATING COILS | [12 empty] | -
| 5.7.6.4 | 5-131 | Furnace Fuel Heating Part Load Efficiency Curve | CoilHtg | FurnHIR_fPLRCrvRef | Furnace | Furn |  | DOE2, E+ | FURN-EFF-FHPLC | Coil:Heating:Gas | Part Load Fraction Correlation Curve | CoilHtgFurnFIRRatio_fQRatio | Quadratic | FIRRatio | QRatio |  |  |  |  | 0.01861 | 1.0942 | -0.11282 | [8 empty] | 1 | 0.73 | 1 | 0.7 |  |  |  | 1 | CrvQuad "CoilHtgFurnFIRRatio_fQRatio" Coef1 = 0.018610 Coef2 = 1.094209 Coef3 = -0.112819 MaxOut = 1.000 MinOut = 0.730 MaxVar1 = 1.000 MinVar1 = 0.700 .. | CrvQuad "CoilHtgFurnFIRRatio_fQRatio" Coef1 = 0.018610 Coef2 = 1.094209 Coef3 = -0.112819 | MaxOut = 1.000 MinOut = 0.730 MaxVar1 = 1.000 MinVar1 = 0.700 | .. | CrvQuad |  | "CoilHtgFurnFIRRatio_fQRatio" |  | 0.018610 | 1.094209 | -0.112819 | - | - | - |  | 1.000 | 0.730 | 1.000 | 0.700 | - | - | QRatio |  | 1 |  | 1 | 0.7 |  |  | 1 | 1 | 0.72927
| 5.7.6.5 | 5-133 | Electric Heat Pump Heating Capacity Adjustment Curve | CoilHtg | HtPumpCap_fTempCrvRef | Air-Source HP | HP | IP | DOE2 | HP-CAP-FT |  |  | CoilHtgHPQRatio_fToadbIP | Cubic | QRatio | Toadb |  |  |  |  | 0.25367 | 0.010435 | 0.0001861 | -1.5e-06 | [7 empty] | 1.05 | 0.17 | 50 |  |  |  |  | 0 | [21 empty] | Toadb |  | 47 |  | 50 | -10 |  |  | 0.99948 | 1.0532 | 0.16943
|  |  |  | CoilHtg | HtPumpCap_fTempCrvRef | Air-Source HP | HP | SI | E+ |  | Coil:Heating:DX:SingleSpeed | Total Heating Capacity Function of Temperature Curve | CoilHtgHPQRatio_fToadbSI | Cubic | QRatio | Toadb |  |  |  |  | 0.72901 | 0.031927 | 0.0001364 | -8.748e-06 | [7 empty] | 1.05 | 0.17 | 10 |  |  |  |  | 1 | CrvCubic "CoilHtgHPQRatio_fToadbSI" Coef1 = 0.729009 Coef2 = 0.031928 Coef3 = 0.000136 Coef4 = -0.000009 MaxOut = 1.050 MinOut = 0.170 MaxVar1 = 10.000 .. | CrvCubic "CoilHtgHPQRatio_fToadbSI" Coef1 = 0.729009 Coef2 = 0.031928 Coef3 = 0.000136 Coef4 = -0.000009 | MaxOut = 1.050 MinOut = 0.170 MaxVar1 = 10.000 | .. | CrvCubic |  | "CoilHtgHPQRatio_fToadbSI" |  | 0.729009 | 0.031928 | 0.000136 | -0.000009 | - | - |  | 1.050 | 0.170 | 10.000 | - | - | - | Toadb |  | 8.3333 |  | 10 | -23.3333 |  |  | 0.99948 | 1.0532 | 0.16943
|  |  |  | CoilHtg | HtPumpCap_fTempCrvRef | Water-source HP | WSHP | IP | DOE2 | HP-CAP-FT |  |  | CoilHtgWSHPQRatio_fTdbTcwsIP | BiLinear | QRatio | Tdb | Tcws |  |  |  | 0.48865 | -0.0067774 | 0 | 0.014082 | [14 empty] | 0 | [21 empty] | Tdb | Tcws
|  |  |  | CoilHtg | HtPumpCap_fTempCrvRef | Water-source HP | WSHP | SI | E+ |  | Coil:Heating:WaterToAirHeatPump:EquationFit | Heating Capacity Coefficient 1-5 | CoilHtgWSHPQRatio_fTdbRatioTwtRatioCFMRatioGPMRatioSI | QuadLinear | QRatio | TdbRatio | TwtRatio | CFMRatio | GPMRatio |  | 0.20487 | -2.8927 | 3.2787 | 0.15436 | 0.11078 | [13 empty] | 0 | [21 empty] | TdbRatio | TwtRatio
| E+ IO Ref | IO p. 1288 | NONE | CoilHtg | HtPumpCap_fFlowCrvRef | Air-Source HP | HP |  | E+ |  | Coil:Heating:DX:SingleSpeed | Total Heating Capacity Function of Flow Fraction Curve | CoilHtgHPQRatio_fCFMRatio | Quadratic | QRatio | CFMRatio |  |  |  |  | 0.84 | 0.16 | 0 | [9 empty] | 0.84 |  |  |  |  | DR: Added; from HeatPump.idf example file | 1 | CrvQuad "CoilHtgHPQRatio_fCFMRatio" Coef1 = 0.840000 Coef2 = 0.160000 Coef3 = 0.000000 MinOut = 0.840 .. | CrvQuad "CoilHtgHPQRatio_fCFMRatio" Coef1 = 0.840000 Coef2 = 0.160000 Coef3 = 0.000000 | MinOut = 0.840 | .. | CrvQuad |  | "CoilHtgHPQRatio_fCFMRatio" |  | 0.840000 | 0.160000 | 0.000000 | - | - | - |  | - | 0.840 | - | - | - | - | CFMRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.84
| 5.7.6.5 | 5-135 | Electric Heat Pump Heating Efficiency Temperature Adjustment Curve(s) | CoilHtg | HtPumpEIR_fTempCrvRef | Air-Source HP | HP | IP | DOE2 | HP-EIR-FT |  |  | CoilHtgHPEIRRatio_fToadbIP | Cubic | EIRRatio | Toadb |  |  |  |  | 2.46 | -0.062254 | 0.00088 | -4.6e-06 | [7 empty] | 3.18 | 0.97 | 50 |  |  |  |  | 0 | [21 empty] | Toadb |  | 47 |  | 50 | -10 |  |  | 1.0004 | 3.1752 | 0.97233 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilHtg | HtPumpEIR_fTempCrvRef | Air-Source HP | HP | SI | E+ |  | Coil:Heating:DX:SingleSpeed | Energy Input Ratio Function of Temperature Curve | CoilHtgHPEIRRatio_fToadbSI | Cubic | EIRRatio | Toadb |  |  |  |  | 1.2183 | -0.036117 | 0.0014204 | -2.6827e-05 | [7 empty] | 3.18 | 0.97 | 10 |  |  |  |  | 1 | CrvCubic "CoilHtgHPEIRRatio_fToadbSI" Coef1 = 1.218290 Coef2 = -0.036117 Coef3 = 0.001420 Coef4 = -0.000027 MaxOut = 3.180 MinOut = 0.970 MaxVar1 = 10.000 .. | CrvCubic "CoilHtgHPEIRRatio_fToadbSI" Coef1 = 1.218290 Coef2 = -0.036117 Coef3 = 0.001420 Coef4 = -0.000027 | MaxOut = 3.180 MinOut = 0.970 MaxVar1 = 10.000 | .. | CrvCubic |  | "CoilHtgHPEIRRatio_fToadbSI" |  | 1.218290 | -0.036117 | 0.001420 | -0.000027 | - | - |  | 3.180 | 0.970 | 10.000 | - | - | - | Toadb |  | 8.3333 |  | 10 | -23.3333 |  |  | 1.0004 | 3.1752 | 0.97233 | Max/MinVar switch to get Max/MinOut
|  |  |  | CoilHtg | HtPumpEIR_fTempCrvRef | Water-Source HP | WSHP | IP | DOE2 | HP-EIR-FT |  |  | CoilHtgWSHPEIRRatio_fTdbTcwsIP | BiLinear | EIRRatio | Tdb | Tcws |  |  |  | 1.3876 | 0.0060479 | 0 | -0.011585 | [14 empty] | 0 | [21 empty] | Tdb | Tcws
|  |  |  | CoilHtg | HtPumpEIR_fTempCrvRef | Water-Source HP | WSHP | SI | E+ |  | Coil:Heating:WaterToAirHeatPump:EquationFit | Heating Power Consumption Coefficient 1-5 | CoilHtgWSHPEIRRatio_fTdbRatioTwtRatioCFMRatioGPMRatioSI | QuadLinear | EIRRatio | TdbRatio | TwtRatio | CFMRatio | GPMRatio |  | -3.5732 | 3.1928 | 1.4157 | -0.16742 | -0.09714 | [13 empty] | 0 | [21 empty] | TdbRatio | TwtRatio
| 5.7.6.5 | 5-135 | Electric Heat Pump Part-Load Efficiency Adjustment Curve(s) | CoilHtg | HtPumpEIR_fPLRCrvRef | Air-Source HP | HP |  | DOE2 | HP-EIR-FPLR |  |  | CoilHtgHPEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  |  |  |  | 0.085652 | 0.93881 | -0.18344 | 0.15897 | [8 empty] | 0.09 | [5 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.085652
|  |  |  | CoilHtg | HtPumpEIR_fPLFCrvRef | Air-Source HP | HP |  | E+ |  | Coil:Heating:DX:SingleSpeed | Energy Input Ratio Function of Flow Fraction Curve | CoilHtgHPEIRRatio_fCFMRatio | Quadratic | EIRRatio | CFMRatio |  |  |  |  | 1.3824 | -0.4336 | 0.0512 | [9 empty] | 1.38 | 1 |  |  |  | DR: Added, from HeatPump.idf example file | 1 | CrvQuad "CoilHtgHPEIRRatio_fCFMRatio" Coef1 = 1.382400 Coef2 = -0.433600 Coef3 = 0.051200 MinOut = 1.380 MaxVar1 = 1.000 .. | CrvQuad "CoilHtgHPEIRRatio_fCFMRatio" Coef1 = 1.382400 Coef2 = -0.433600 Coef3 = 0.051200 | MinOut = 1.380 MaxVar1 = 1.000 | .. | CrvQuad |  | "CoilHtgHPEIRRatio_fCFMRatio" |  | 1.382400 | -0.433600 | 0.051200 | - | - | - |  | - | 1.380 | 1.000 | - | - | - | CFMRatio |  | 1 |  | 1 | 0 |  |  | 1 |  | 1.3824
|  |  |  | CoilHtg | HtPumpEIR_fFlowCrvRef | Air-Source HP | HP |  | E+ |  | Coil:Heating:DX:SingleSpeed | Part Load Fraction Correlation Curve | CoilHtgHPEIRRatio_fQFrac | Quadratic | EIRRatio | QFrac |  |  |  |  | 0.85 | 0.15 | 0 | [8 empty] | 1 | 0.85 | 1 |  |  |  | DR: Added, from HeatPump.idf example file | 1 | CrvQuad "CoilHtgHPEIRRatio_fQFrac" Coef1 = 0.850000 Coef2 = 0.150000 Coef3 = 0.000000 MaxOut = 1.000 MinOut = 0.850 MaxVar1 = 1.000 .. | CrvQuad "CoilHtgHPEIRRatio_fQFrac" Coef1 = 0.850000 Coef2 = 0.150000 Coef3 = 0.000000 | MaxOut = 1.000 MinOut = 0.850 MaxVar1 = 1.000 | .. | CrvQuad |  | "CoilHtgHPEIRRatio_fQFrac" |  | 0.850000 | 0.150000 | 0.000000 | - | - | - |  | 1.000 | 0.850 | 1.000 | - | - | - | QFrac |  | 1 |  | 1 | 0 |  |  | 1 | 1 | 0.85
EVAP COOLERS | [12 empty] | -
| 5.7.5.3 | 5-129 | Evaporative Cooling Performance Curves | EvapClr | Eff_fPLRCrvRef | Direct Evap Cooler | Direct |  | DOE2 | EVAP-EFF-FFLOW |  |  | EvapClrDirectEffRatio_fCFMRatio | Quadratic | EffRatio | CFMRatio |  |  |  |  | 1.1833 | -0.25753 | 0.074245 | [9 empty] | 1.18 | [5 empty] | 0 | [21 empty] | CFMRatio |  | 1 |  |  | 0 |  |  | 1 |  | 1.1833
|  |  |  | EvapClr |  | Indirect Evap Cooler | Indirect |  | DOE2 |  |  |  | EvapClrIndirectEffRatio_fCFMRatio | Quadratic | EffRatio | CFMRatio |  |  |  |  | 1.097 | -0.16506 | 0.068069 | [9 empty] | 1.1 | [5 empty] | 0 | [21 empty] | CFMRatio |  | 1 |  |  | 0 |  |  | 1 |  | 1.097
BOILERS | [12 empty] | -
| 5.8.1 | 5-150 | Boiler Part-Load Performance Curve | Blr | HI_fPLRCrvRef | Hot Water Boiler, Non-Nondensing | HWBlr | IP | DOE2 | HIR-FPLR | Boiler:HotWater | Normalized Boiler Efficiency Curve | BlrHWBlrFIRRatio_fQRatioIP | Quadratic | FIRRatio | QRatio |  |  |  |  | 0.082597 | 0.99676 | -0.079361 | [9 empty] | 0.08 | [5 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.082597
|  |  |  | Blr | HIR_fPLRCrvRef | Hot Water Boiler, Non-Nondensing | HWBlr | SI | E+ | HIR-FPLR | Boiler:HotWater | Normalized Boiler Efficiency Curve | BlrHWBlrFIRRatio_fQRatioSI | Quadratic | FIRRatio | QRatio |  |  |  |  | 0.6267 | 0.674 | -0.3073 | [9 empty] | 0.75 |  | 0.2 |  |  |  | 1 | CrvQuad "BlrHWBlrFIRRatio_fQRatioSI" Coef1 = 0.626700 Coef2 = 0.674000 Coef3 = -0.307300 MinOut = 0.750 MinVar1 = 0.200 .. | CrvQuad "BlrHWBlrFIRRatio_fQRatioSI" Coef1 = 0.626700 Coef2 = 0.674000 Coef3 = -0.307300 | MinOut = 0.750 MinVar1 = 0.200 | .. | CrvQuad |  | "BlrHWBlrFIRRatio_fQRatioSI" |  | 0.626700 | 0.674000 | -0.307300 | - | - | - |  | - | 0.750 | - | 0.200 | - | - | QRatio |  | 1 |  | 1 | 0.2 |  |  | 0.9934 |  | 0.74921
|  |  |  | Blr | HI_fPLRCrvRef | Hot Water Boiler, Condensing | HWCondBlr | IP | DOE2 | HIR-FT |  |  | BlrHWCondBlrFIRRatio_fQRatioTewtIP | BiQuadratic | FIRRatio | QRatio | Tewt | [16 empty] | 1 |  |  |  |  | 0 | [21 empty] | QRatio | Tewt | 1 |  | 1 | 0 |  |  | 0 |  | 0
|  |  |  | Blr | HIR_fPLRfTempCrvRef | Hot Water Boiler, Condensing | HWCondBlr | SI | E+ | HIR-FPLR-FT | Boiler:HotWater | Normalized Boiler Efficiency Curve | BlrHWCondBlrFIRRatio_fQRatioTewtSI | BiQuadratic | FIRRatio | QRatio | Tewt |  |  |  | 1.1938 | -0.11083 | 0.039514 | -0.0063714 | 3.8135e-05 | 0.00083038 | [5 empty] | 1.05 | 0.93 | 1 | 0.1 | 71.1 | 15.56 | Field: Efficiency Curve Temperature Evaluation Variable must be defined as 'EnteringBoiler' | 1 | CrvDblQuad "BlrHWCondBlrFIRRatio_fQRatioTewtSI" Coef1 = 1.193810 Coef2 = -0.110825 Coef3 = 0.039514 Coef4 = -0.006371 Coef5 = 0.000038 Coef6 = 0.000830 MaxOut = 1.050 MinOut = 0.930 MaxVar1 = 1.000 MinVar1 = 0.100 MaxVar2 = 71.100 MinVar2 = 15.560 .. | CrvDblQuad "BlrHWCondBlrFIRRatio_fQRatioTewtSI" Coef1 = 1.193810 Coef2 = -0.110825 Coef3 = 0.039514 Coef4 = -0.006371 Coef5 = 0.000038 Coef6 = 0.000830 | MaxOut = 1.050 MinOut = 0.930 MaxVar1 = 1.000 MinVar1 = 0.100 MaxVar2 = 71.100 MinVar2 = 15.560 | .. | CrvDblQuad |  | "BlrHWCondBlrFIRRatio_fQRatioTewtSI" |  | 1.193810 | -0.110825 | 0.039514 | -0.006371 | 0.000038 | 0.000830 |  | 1.050 | 0.930 | 1.000 | 0.100 | 71.100 | 15.560 | QRatio | Tewt | 1 | 26.7 | 1 | 0.1 | 71.1 | 15.5556 | 1.0017 | 1.0455 | 0.9288 |  | BlrEff | 0.95 | 0.99326 | 0.88236 | Larger value = more eff
ELECTRIC CHILLERS | [12 empty] | -
| 5.8.2 | 5-154 | Chiller Cooling Capacity Adjustment Curves | Chlr | Cap_fTempCrvRef | Air-Cooled Scroll | AirScroll | IP | DOE2 | CH-CAP-FT |  |  | ChlrAirScrollQRatio_fTchwsToadbIP | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | 0.40071 | 0.018615 | 7.199e-05 | 0.001773 | -2.014e-05 | -8.273e-05 | [5 empty] | 1.3 | 0.82 | 54 | 40 | 115 | 75 |  | 0 | [21 empty] | Tchws | Toadb | 44 | 95 | 54 | 40 | 115 | 75 | 1 | 1.3005 | 0.81749 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Scroll | AirScroll | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrAirScrollQRatio_fTchwsToadbSI | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | 1.0214 | 0.037021 | 0.00023328 | -0.0038934 | -6.48e-05 | -0.00026892 | [5 empty] | 1.3 | 0.82 | 12.22 | 4.44 | 46.11 | 23.89 |  | 1 | CrvDblQuad "ChlrAirScrollQRatio_fTchwsToadbSI" Coef1 = 1.021380 Coef2 = 0.037021 Coef3 = 0.000233 Coef4 = -0.003893 Coef5 = -0.000065 Coef6 = -0.000269 MaxOut = 1.300 MinOut = 0.820 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "ChlrAirScrollQRatio_fTchwsToadbSI" Coef1 = 1.021380 Coef2 = 0.037021 Coef3 = 0.000233 Coef4 = -0.003893 Coef5 = -0.000065 Coef6 = -0.000269 | MaxOut = 1.300 MinOut = 0.820 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "ChlrAirScrollQRatio_fTchwsToadbSI" |  | 1.021380 | 0.037021 | 0.000233 | -0.003893 | -0.000065 | -0.000269 |  | 1.300 | 0.820 | 12.220 | 4.440 | 46.110 | 23.890 |  |  | 6.6667 | 35 | 12.2222 | 4.4444 | 46.1111 | 23.8889 | 1.0002 | 1.3002 | 0.8181 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Recip | AirRecip | IP | DOE2 | CH-CAP-FT |  |  | ChlrAirRecipQRatio_fTchwsToadbIP | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | 0.57617 | 0.020631 | 7.769e-05 | -0.0035118 | 3.12e-06 | -7.865e-05 | [5 empty] | 1.35 | 0.8 | 54 | 40 | 115 | 75 |  | 0 | [23 empty] | 44 | 95 | 54 | 40 | 115 | 75 | 1.0001 | 1.3524 | 0.80134 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Recip | AirRecip | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrAirRecipQRatio_fTchwsToadbSI | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | 1.126 | 0.041571 | 0.00025272 | -0.010526 | 9.72e-06 | -0.00025596 | [5 empty] | 1.35 | 0.8 | 12.22 | 4.44 | 46.11 | 23.89 |  | 1 | CrvDblQuad "ChlrAirRecipQRatio_fTchwsToadbSI" Coef1 = 1.126030 Coef2 = 0.041571 Coef3 = 0.000253 Coef4 = -0.010526 Coef5 = 0.000010 Coef6 = -0.000256 MaxOut = 1.350 MinOut = 0.800 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "ChlrAirRecipQRatio_fTchwsToadbSI" Coef1 = 1.126030 Coef2 = 0.041571 Coef3 = 0.000253 Coef4 = -0.010526 Coef5 = 0.000010 Coef6 = -0.000256 | MaxOut = 1.350 MinOut = 0.800 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "ChlrAirRecipQRatio_fTchwsToadbSI" |  | 1.126030 | 0.041571 | 0.000253 | -0.010526 | 0.000010 | -0.000256 |  | 1.350 | 0.800 | 12.220 | 4.440 | 46.110 | 23.890 | Tchws | Toadb | 6.6667 | 35 | 12.2222 | 4.4444 | 46.1111 | 23.8889 | 0.99816 | 1.3512 | 0.79861 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Screw | AirScrew | IP | DOE2 | CH-CAP-FT |  |  | ChlrAirScrewQRatio_fTchwsToadbIP | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | -0.094649 | 0.038341 | -9.205e-05 | 0.0037801 | -1.375e-05 | -0.00015464 | [5 empty] | 1.29 | 0.83 | 54 | 40 | 115 | 75 |  | 0 | [21 empty] | Tchws | Toadb | 44 | 95 | 54 | 40 | 115 | 75 | 1.0028 | 1.2872 | 0.83322 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Screw | AirScrew | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrAirScrewQRatio_fTchwsToadbSI | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | 0.98596 | 0.049487 | -0.00029808 | -0.0037368 | -4.536e-05 | -0.0005022 | [5 empty] | 1.28 | 0.83 | 12.22 | 4.44 | 46.11 | 23.89 |  | 1 | CrvDblQuad "ChlrAirScrewQRatio_fTchwsToadbSI" Coef1 = 0.985959 Coef2 = 0.049487 Coef3 = -0.000298 Coef4 = -0.003737 Coef5 = -0.000045 Coef6 = -0.000502 MaxOut = 1.280 MinOut = 0.830 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "ChlrAirScrewQRatio_fTchwsToadbSI" Coef1 = 0.985959 Coef2 = 0.049487 Coef3 = -0.000298 Coef4 = -0.003737 Coef5 = -0.000045 Coef6 = -0.000502 | MaxOut = 1.280 MinOut = 0.830 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "ChlrAirScrewQRatio_fTchwsToadbSI" |  | 0.985959 | 0.049487 | -0.000298 | -0.003737 | -0.000045 | -0.000502 |  | 1.280 | 0.830 | 12.220 | 4.440 | 46.110 | 23.890 | Tchws | Toadb | 6.6667 | 35 | 12.2222 | 4.4444 | 46.1111 | 23.8889 | 0.99909 | 1.2845 | 0.82834 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Centrifugal | AirCent | IP | DOE2 | CH-CAP-FT |  |  | ChlrAirCentQRatio_fTchwsToadbIP | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | 0 | [21 empty] | Tchws | Toadb
|  |  |  | Chlr | Cap_fTempCrvRef | Air-Cooled Centrifugal | AirCent | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrAirCentQRatio_fTchwsToadbSI | BiQuadratic | QRatio | Tchws | Toadb |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | 0 | [21 empty] | Tchws | Toadb
|  | 5-156 | Electric Chiller Cooling Efficiency Adjustment Curves | Chlr | EIR_fTempCrvRef | Air-Cooled Scroll | AirScroll | IP | DOE2 | CH-EIR-FT |  |  | ChlrAirScrollEIRRatio_fTchwsToadbIP | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | 0.99007 | -0.0058414 | 0.00016454 | -0.0066114 | 0.00016808 | -0.00022501 | [5 empty] | 1.45 | 0.69 | 54 | 40 | 115 | 75 |  | 0 | [21 empty] | Tchws | Toadb | 44 | 95 | 54 | 40 | 115 | 75 | 0.99989 | 1.4472 | 0.69273 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Scroll | AirScroll | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrAirScrollEIRRatio_fTchwsToadbSI | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | 0.70219 | -0.0044658 | 0.0005346 | -0.0055062 | 0.00054432 | -0.000729 | [5 empty] | 1.45 | 0.69 | 12.22 | 4.44 | 46.11 | 23.89 |  | 1 | CrvDblQuad "ChlrAirScrollEIRRatio_fTchwsToadbSI" Coef1 = 0.702194 Coef2 = -0.004466 Coef3 = 0.000535 Coef4 = -0.005506 Coef5 = 0.000544 Coef6 = -0.000729 MaxOut = 1.450 MinOut = 0.690 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "ChlrAirScrollEIRRatio_fTchwsToadbSI" Coef1 = 0.702194 Coef2 = -0.004466 Coef3 = 0.000535 Coef4 = -0.005506 Coef5 = 0.000544 Coef6 = -0.000729 | MaxOut = 1.450 MinOut = 0.690 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "ChlrAirScrollEIRRatio_fTchwsToadbSI" |  | 0.702194 | -0.004466 | 0.000535 | -0.005506 | 0.000544 | -0.000729 |  | 1.450 | 0.690 | 12.220 | 4.440 | 46.110 | 23.890 | Tchws | Toadb | 6.6667 | 35 | 12.2222 | 4.4444 | 46.1111 | 23.8889 | 1.0002 | 1.447 | 0.69372 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Recip | AirRecip | IP | DOE2 | CH-EIR-FT |  |  | ChlrAirRecipEIRRatio_fTchwsToadbIP | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | 0.66534 | -0.013838 | 0.00014736 | 0.0071281 | 4.571e-05 | -0.00010326 | [5 empty] | 1.3 | 0.72 | 54 | 40 | 115 | 75 |  | 0 | [21 empty] | Tchws | Toadb | 44 | 95 | 54 | 40 | 115 | 75 | 0.99983 | 1.2968 | 0.7213 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Recip | AirRecip | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrAirRecipEIRRatio_fTchwsToadbSI | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | 0.54278 | -0.013907 | 0.00047628 | 0.012197 | 0.00014904 | -0.00033372 | [5 empty] | 1.3 | 0.72 | 12.22 | 4.44 | 46.11 | 23.89 |  | 1 | CrvDblQuad "ChlrAirRecipEIRRatio_fTchwsToadbSI" Coef1 = 0.542784 Coef2 = -0.013907 Coef3 = 0.000476 Coef4 = 0.012197 Coef5 = 0.000149 Coef6 = -0.000334 MaxOut = 1.300 MinOut = 0.720 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "ChlrAirRecipEIRRatio_fTchwsToadbSI" Coef1 = 0.542784 Coef2 = -0.013907 Coef3 = 0.000476 Coef4 = 0.012197 Coef5 = 0.000149 Coef6 = -0.000334 | MaxOut = 1.300 MinOut = 0.720 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "ChlrAirRecipEIRRatio_fTchwsToadbSI" |  | 0.542784 | -0.013907 | 0.000476 | 0.012197 | 0.000149 | -0.000334 |  | 1.300 | 0.720 | 12.220 | 4.440 | 46.110 | 23.890 | Tchws | Toadb | 6.6667 | 35 | 12.2222 | 4.4444 | 46.1111 | 23.8889 | 1.0028 | 1.3013 | 0.72294 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Screw | AirScrew | IP | DOE2 | CH-EIR-FT |  |  | ChlrAirScrewEIRRatio_fTchwsToadbIP | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | 0.13546 | 0.022929 | -0.00016107 | -0.002354 | 0.00012991 | -0.00018685 | [5 empty] | 1.38 | 0.7 | 54 | 40 | 115 | 75 |  | 0 | [21 empty] | Tchws | Toadb | 44 | 95 | 54 | 40 | 115 | 75 | 1.0003 | 1.3828 | 0.70142 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Screw | AirScrew | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrAirScrewEIRRatio_fTchwsToadbSI | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | 0.57062 | 0.011954 | -0.00052164 | -3.24e-05 | 0.0004212 | -0.00060588 | [5 empty] | 1.38 | 0.7 | 12.22 | 4.44 | 46.11 | 23.89 |  | 1 | CrvDblQuad "ChlrAirScrewEIRRatio_fTchwsToadbSI" Coef1 = 0.570624 Coef2 = 0.011954 Coef3 = -0.000522 Coef4 = -0.000032 Coef5 = 0.000421 Coef6 = -0.000606 MaxOut = 1.380 MinOut = 0.700 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 .. | CrvDblQuad "ChlrAirScrewEIRRatio_fTchwsToadbSI" Coef1 = 0.570624 Coef2 = 0.011954 Coef3 = -0.000522 Coef4 = -0.000032 Coef5 = 0.000421 Coef6 = -0.000606 | MaxOut = 1.380 MinOut = 0.700 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 46.110 MinVar2 = 23.890 | .. | CrvDblQuad |  | "ChlrAirScrewEIRRatio_fTchwsToadbSI" |  | 0.570624 | 0.011954 | -0.000522 | -0.000032 | 0.000421 | -0.000606 |  | 1.380 | 0.700 | 12.220 | 4.440 | 46.110 | 23.890 | Tchws | Toadb | 6.6667 | 35 | 12.2222 | 4.4444 | 46.1111 | 23.8889 | 1.0006 | 1.3834 | 0.7015 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Centrifugal | AirCent | IP | DOE2 | CH-EIR-FT |  |  | ChlrAirCentEIRRatio_fTchwsToadbIP | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | 0 | [21 empty] | Tchws | Toadb
|  |  |  | Chlr | EIR_fTempCrvRef | Air-Cooled Centrifugal | AirCent | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrAirCentEIRRatio_fTchwsToadbSI | BiQuadratic | EIRRatio | Tchws | Toadb |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | 0 | [21 empty] | Tchws | Toadb
|  | 5-156 | Electric Chiller Cooling Efficiency Adjustment Curves | Chlr | EIR_fPLRCrvRef | Air-Cooled Scroll | AirScroll |  | DOE2, E+ | CH-EIR-FPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrAirScrollEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.063691 | 0.58489 | 0.3528 | [9 empty] | 0.06 | [5 empty] | 1 | CrvQuad "ChlrAirScrollEIRRatio_fQRatio" Coef1 = 0.063691 Coef2 = 0.584888 Coef3 = 0.352803 MinOut = 0.060 .. | CrvQuad "ChlrAirScrollEIRRatio_fQRatio" Coef1 = 0.063691 Coef2 = 0.584888 Coef3 = 0.352803 | MinOut = 0.060 | .. | CrvQuad |  | "ChlrAirScrollEIRRatio_fQRatio" |  | 0.063691 | 0.584888 | 0.352803 | - | - | - |  | - | 0.060 | - | - | - | - | QRatio |  | 1 |  |  | 0 |  |  | 1.0014 |  | 0.063691
|  |  |  | Chlr | EIR_fPLRCrvRef | Air-Cooled Recip | AirRecip |  | DOE2, E+ | CH-EIR-FPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrAirRecipEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.11444 | 0.54593 | 0.3423 | [9 empty] | 0.11 | [5 empty] | 1 | CrvQuad "ChlrAirRecipEIRRatio_fQRatio" Coef1 = 0.114437 Coef2 = 0.545933 Coef3 = 0.342299 MinOut = 0.110 .. | CrvQuad "ChlrAirRecipEIRRatio_fQRatio" Coef1 = 0.114437 Coef2 = 0.545933 Coef3 = 0.342299 | MinOut = 0.110 | .. | CrvQuad |  | "ChlrAirRecipEIRRatio_fQRatio" |  | 0.114437 | 0.545933 | 0.342299 | - | - | - |  | - | 0.110 | - | - | - | - | QRatio |  | 1 |  |  | 0 |  |  | 1.0027 |  | 0.11444
|  |  |  | Chlr | EIR_fPLRCrvRef | Air-Cooled Screw | AirScrew |  | DOE2, E+ | CH-EIR-FPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrAirScrewEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.036487 | 0.73474 | 0.21995 | [9 empty] | 0.04 | [5 empty] | 1 | CrvQuad "ChlrAirScrewEIRRatio_fQRatio" Coef1 = 0.036487 Coef2 = 0.734743 Coef3 = 0.219947 MinOut = 0.040 .. | CrvQuad "ChlrAirScrewEIRRatio_fQRatio" Coef1 = 0.036487 Coef2 = 0.734743 Coef3 = 0.219947 | MinOut = 0.040 | .. | CrvQuad |  | "ChlrAirScrewEIRRatio_fQRatio" |  | 0.036487 | 0.734743 | 0.219947 | - | - | - |  | - | 0.040 | - | - | - | - | QRatio |  | 1 |  |  | 0 |  |  | 0.99118 |  | 0.036487
|  |  |  | Chlr | EIR_fPLRCrvRef | Air-Cooled Centrifugal | AirCent |  | DOE2, E+ | CH-EIR-FPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrAirCentEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | N/A | N/A | N/A | [15 empty] | 0 | [21 empty] | QRatio
ELECTRIC WATER-COOLED CHILLERS (PATH A & B) | [12 empty] | -
|  |  | Chiller Cooling Capacity Adjustment Curves | Chlr | Cap_fTempCrvRef | Water-Cooled Pos Displacement, Path A, All Capacities | WtrPosDispPathAAll | IP | DOE2 | Cap-fCHWT&ECT |  |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.4468 | 0.014742 | 0.00013391 | 0.00044024 | -1.5214e-05 | -8.4707e-05 | [5 empty] | 1.33 | 0.89 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 0.9654 | 1.3305 | 0.89023 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Pos Displacement, Path A, All Capacities | WtrPosDispPathAAll | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.96744 | 0.037082 | 0.00043384 | -0.0058374 | -4.9248e-05 | -0.00027443 | [5 empty] | 1.33 | 0.89 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI" Coef1 = 0.967440 Coef2 = 0.037082 Coef3 = 0.000434 Coef4 = -0.005837 Coef5 = -0.000049 Coef6 = -0.000274 MaxOut = 1.330 MinOut = 0.890 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI" Coef1 = 0.967440 Coef2 = 0.037082 Coef3 = 0.000434 Coef4 = -0.005837 Coef5 = -0.000049 Coef6 = -0.000274 | MaxOut = 1.330 MinOut = 0.890 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI" |  | 0.967440 | 0.037082 | 0.000434 | -0.005837 | -0.000049 | -0.000274 |  | 1.330 | 0.890 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 0.96549 | 1.3306 | 0.89033 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifugal, Path A, All Capacities | WtrCentPathAAll | IP | DOE2 | Cap-fCHWT&ECT |  |  | ChlrWtrCentPathAAllQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | -0.49737 | -0.0095607 | -0.00059561 | 0.043521 | -0.00058394 | 0.00096007 | [5 empty] | 0.87 | 0.91 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 0.99983 | 0.86925 | 0.91178 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifugal, Path A, All Capacities | WtrCentPathAAll | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.36469 | -0.030521 | -0.0019297 | 0.066374 | -0.0018918 | 0.0031107 | [5 empty] | 0.87 | 0.91 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI" Coef1 = 0.364691 Coef2 = -0.030521 Coef3 = -0.001930 Coef4 = 0.066374 Coef5 = -0.001892 Coef6 = 0.003111 MaxOut = 0.870 MinOut = 0.910 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI" Coef1 = 0.364691 Coef2 = -0.030521 Coef3 = -0.001930 Coef4 = 0.066374 Coef5 = -0.001892 Coef6 = 0.003111 | MaxOut = 0.870 MinOut = 0.910 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI" |  | 0.364691 | -0.030521 | -0.001930 | 0.066374 | -0.001892 | 0.003111 |  | 0.870 | 0.910 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 1.0003 | 0.86952 | 0.91218 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Positive Displacement, Path B, All Capacities | WtrPosDispPathBAll | IP | DOE2 | Cap-fCHWT&ECT |  |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.33413 | 0.021015 | -0.0001024 | -0.001407 | -2.8516e-05 | 7.0706e-05 | [5 empty] | 1.21 | 0.93 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 0.99934 | 1.2123 | 0.92565 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Positive Displacement, Path B, All Capacities | WtrPosDispPathBAll | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.89993 | 0.030102 | -0.00033178 | -0.0017435 | -9.234e-05 | 0.00022907 | [5 empty] | 1.21 | 0.93 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI" Coef1 = 0.899926 Coef2 = 0.030102 Coef3 = -0.000332 Coef4 = -0.001743 Coef5 = -0.000092 Coef6 = 0.000229 MaxOut = 1.210 MinOut = 0.930 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI" Coef1 = 0.899926 Coef2 = 0.030102 Coef3 = -0.000332 Coef4 = -0.001743 Coef5 = -0.000092 Coef6 = 0.000229 | MaxOut = 1.210 MinOut = 0.930 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI" |  | 0.899926 | 0.030102 | -0.000332 | -0.001743 | -0.000092 | 0.000229 |  | 1.210 | 0.930 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 0.99943 | 1.2124 | 0.92574 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifugal, Path B, <300ton | WtrCentPathBLt300ton | IP | DOE2 | Cap-fCHWT&ECT |  |  | ChlrWtrCentPathBLt300tonQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.18098 | 0.031844 | -0.00015415 | 0.0095659 | -0.00013547 | -5.3197e-05 | [5 empty] | 1.36 | 0.86 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 0.91907 | 1.365 | 0.86157 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifugal, Path B, <300ton | WtrCentPathBLt300ton | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrWtrCentPathBLt300tonQRatio_fTchwsTcwsSI | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 1.1551 | 0.036503 | -0.00049928 | -0.0014553 | -0.00043902 | -0.00017237 | [5 empty] | 1.37 | 0.86 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathBLt300tonQRatio_fTchwsTcwsSI" Coef1 = 1.155080 Coef2 = 0.036503 Coef3 = -0.000499 Coef4 = -0.001455 Coef5 = -0.000439 Coef6 = -0.000172 MaxOut = 1.370 MinOut = 0.860 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathBLt300tonQRatio_fTchwsTcwsSI" Coef1 = 1.155080 Coef2 = 0.036503 Coef3 = -0.000499 Coef4 = -0.001455 Coef5 = -0.000439 Coef6 = -0.000172 | MaxOut = 1.370 MinOut = 0.860 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathBLt300tonQRatio_fTchwsTcwsSI" |  | 1.155080 | 0.036503 | -0.000499 | -0.001455 | -0.000439 | -0.000172 |  | 1.370 | 0.860 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 0.91894 | 1.365 | 0.86143 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifugal, Path B, 300-600ton | WtrCentPathBGtEql300Lt600ton | IP | DOE2 | Cap-fCHWT&ECT |  |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.36396 | 0.045022 | -0.00027422 | -0.002028 | -8.8275e-05 | -1.2166e-05 | [5 empty] | 1.52 | 0.87 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 0.95838 | 1.5167 | 0.87457 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifugal, Path B, 300-600ton | WtrCentPathBGtEql300Lt600ton | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 1.3561 | 0.04875 | -0.00088841 | -0.014525 | -0.00028609 | -3.9528e-05 | [5 empty] | 1.52 | 0.87 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI" Coef1 = 1.356080 Coef2 = 0.048750 Coef3 = -0.000888 Coef4 = -0.014525 Coef5 = -0.000286 Coef6 = -0.000040 MaxOut = 1.520 MinOut = 0.870 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI" Coef1 = 1.356080 Coef2 = 0.048750 Coef3 = -0.000888 Coef4 = -0.014525 Coef5 = -0.000286 Coef6 = -0.000040 | MaxOut = 1.520 MinOut = 0.870 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI" |  | 1.356080 | 0.048750 | -0.000888 | -0.014525 | -0.000286 | -0.000040 |  | 1.520 | 0.870 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 0.95811 | 1.5165 | 0.8743 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifuga, Path B, >600ton | WtrCentPathBGtEql600ton | IP | DOE2 | Cap-fCHWT&ECT |  |  | ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | -0.4552 | 0.031347 | -5.715e-05 | 0.020383 | -0.00015341 | -0.00012709 | [5 empty] | 1.33 | 0.9 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 0.96225 | 1.3298 | 0.89927 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | Cap_fTempCrvRef | Water-Cooled Centrifuga, Path B, >600ton | WtrCentPathBGtEql600ton | SI | E+ |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.85445 | 0.042526 | -0.000185 | 0.011697 | -0.00049702 | -0.0004118 | [5 empty] | 1.33 | 0.9 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI" Coef1 = 0.854454 Coef2 = 0.042526 Coef3 = -0.000185 Coef4 = 0.011697 Coef5 = -0.000497 Coef6 = -0.000412 MaxOut = 1.330 MinOut = 0.900 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI" Coef1 = 0.854454 Coef2 = 0.042526 Coef3 = -0.000185 Coef4 = 0.011697 Coef5 = -0.000497 Coef6 = -0.000412 | MaxOut = 1.330 MinOut = 0.900 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI" |  | 0.854454 | 0.042526 | -0.000185 | 0.011697 | -0.000497 | -0.000412 |  | 1.330 | 0.900 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 0.96241 | 1.33 | 0.89942 | Max/MinVar switch to get Max/MinOut
|  |  | Electric Chiller Cooling Efficiency Adjustment Curves | Chlr | EIR_fTempCrvRef | Water-Cooled Pos Displacement, Path A, All Capacities | WtrPosDispPathAAll | IP | DOE2 | EIR-fCHWT&ECT |  |  | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsIP | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.71399 | -0.0061933 | 0.0001491 | 0.0030655 | 0.00016787 | -0.0002668 | [5 empty] | 1.27 | 0.74 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 1.2057 | 1.2711 | 0.73816 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Pos Displacement, Path A, All Capacities | WtrPosDispPathAAll | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.66531 | -0.0093393 | 0.00048308 | 0.0094923 | 0.000544 | -0.00086443 | [5 empty] | 1.27 | 0.74 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI" Coef1 = 0.665307 Coef2 = -0.009339 Coef3 = 0.000483 Coef4 = 0.009492 Coef5 = 0.000544 Coef6 = -0.000864 MaxOut = 1.270 MinOut = 0.740 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI" Coef1 = 0.665307 Coef2 = -0.009339 Coef3 = 0.000483 Coef4 = 0.009492 Coef5 = 0.000544 Coef6 = -0.000864 | MaxOut = 1.270 MinOut = 0.740 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI" |  | 0.665307 | -0.009339 | 0.000483 | 0.009492 | 0.000544 | -0.000864 |  | 1.270 | 0.740 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 1.206 | 1.2713 | 0.73827 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifugal, Path A, All Capacities | WtrCentPathAAll | IP | DOE2 | EIR-fCHWT&ECT |  |  | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsIP | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 1.1536 | -0.030679 | 0.00030591 | 0.0067087 | 5.28e-05 | -9.297e-05 | [5 empty] | 1.05 | 0.68 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 1 | 1.0515 | 0.68036 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifugal, Path A, All Capacities | WtrCentPathAAll | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.65864 | -0.025339 | 0.00099112 | 0.012801 | 0.00017107 | -0.00030132 | [5 empty] | 1.05 | 0.68 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI" Coef1 = 0.658643 Coef2 = -0.025339 Coef3 = 0.000991 Coef4 = 0.012801 Coef5 = 0.000171 Coef6 = -0.000301 MaxOut = 1.050 MinOut = 0.680 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI" Coef1 = 0.658643 Coef2 = -0.025339 Coef3 = 0.000991 Coef4 = 0.012801 Coef5 = 0.000171 Coef6 = -0.000301 | MaxOut = 1.050 MinOut = 0.680 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI" |  | 0.658643 | -0.025339 | 0.000991 | 0.012801 | 0.000171 | -0.000301 |  | 1.050 | 0.680 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 0.99986 | 1.0514 | 0.68024 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Positive Displacement, Path B, All Capacities | WtrPosDispPathBAll | IP | DOE2 | EIR-fCHWT&ECT |  |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsIP | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.76681 | -0.024317 | 0.00026197 | 0.0074109 | 0.00011772 | -0.00018203 | [5 empty] | 1.07 | 0.5 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 1.0037 | 1.0748 | 0.49624 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Positive Displacement, Path B, All Capacities | WtrPosDispPathBAll | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.42827 | -0.024071 | 0.00084888 | 0.016415 | 0.00038135 | -0.00058968 | [5 empty] | 1.07 | 0.5 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI" Coef1 = 0.428265 Coef2 = -0.024071 Coef3 = 0.000849 Coef4 = 0.016416 Coef5 = 0.000381 Coef6 = -0.000590 MaxOut = 1.070 MinOut = 0.500 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI" Coef1 = 0.428265 Coef2 = -0.024071 Coef3 = 0.000849 Coef4 = 0.016416 Coef5 = 0.000381 Coef6 = -0.000590 | MaxOut = 1.070 MinOut = 0.500 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI" |  | 0.428265 | -0.024071 | 0.000849 | 0.016416 | 0.000381 | -0.000590 |  | 1.070 | 0.500 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 1.0037 | 1.0748 | 0.49639 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifugal, Path B, <300ton | WtrCentPathBLt300ton | IP | DOE2 | EIR-fCHWT&ECT |  |  | ChlrWtrCentPathBLt300tonEIRRatio_fTchwsTcwsIP | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.87311 | -0.025208 | 0.00036862 | 0.018292 | 4.7035e-05 | -0.00035766 | [5 empty] | 1.13 | 0.69 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 1.0346 | 1.1332 | 0.69484 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifugal, Path B, <300ton | WtrCentPathBLt300ton | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrWtrCentPathBLt300tonEIRRatio_fTchwsTcwsSI | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.71111 | -0.023515 | 0.0011943 | 0.017737 | 0.00015228 | -0.0011589 | [5 empty] | 1.13 | 0.69 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathBLt300tonEIRRatio_fTchwsTcwsSI" Coef1 = 0.711108 Coef2 = -0.023515 Coef3 = 0.001194 Coef4 = 0.017737 Coef5 = 0.000152 Coef6 = -0.001159 MaxOut = 1.130 MinOut = 0.690 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathBLt300tonEIRRatio_fTchwsTcwsSI" Coef1 = 0.711108 Coef2 = -0.023515 Coef3 = 0.001194 Coef4 = 0.017737 Coef5 = 0.000152 Coef6 = -0.001159 | MaxOut = 1.130 MinOut = 0.690 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathBLt300tonEIRRatio_fTchwsTcwsSI" |  | 0.711108 | -0.023515 | 0.001194 | 0.017737 | 0.000152 | -0.001159 |  | 1.130 | 0.690 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 1.0342 | 1.1328 | 0.69452 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifugal, Path B, 300-600ton | WtrCentPathBGtEql300Lt600ton | IP | DOE2 | EIR-fCHWT&ECT |  |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsIP | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.97432 | -0.0046317 | 4.8004e-05 | -0.0020126 | 0.00015875 | -0.00021199 | [5 empty] | 1.12 | 0.63 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 1.0465 | 1.121 | 0.6281 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifugal, Path B, 300-600ton | WtrCentPathBGtEql300Lt600ton | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.75638 | -0.015019 | 0.00015552 | 0.0024599 | 0.00051451 | -0.00068688 | [5 empty] | 1.12 | 0.63 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI" Coef1 = 0.756376 Coef2 = -0.015019 Coef3 = 0.000156 Coef4 = 0.002460 Coef5 = 0.000515 Coef6 = -0.000687 MaxOut = 1.120 MinOut = 0.630 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI" Coef1 = 0.756376 Coef2 = -0.015019 Coef3 = 0.000156 Coef4 = 0.002460 Coef5 = 0.000515 Coef6 = -0.000687 | MaxOut = 1.120 MinOut = 0.630 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI" |  | 0.756376 | -0.015019 | 0.000156 | 0.002460 | 0.000515 | -0.000687 |  | 1.120 | 0.630 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 1.0468 | 1.1213 | 0.62822 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifuga, Path B, >600ton | WtrCentPathBGtEql600ton | IP | DOE2 | EIR-fCHWT&ECT |  |  | ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsIP | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.36702 | 0.012466 | -6.8823e-05 | 0.005934 | 8.2447e-05 | -0.00022665 | [5 empty] | 1.09 | 0.76 | 54 | 40 | 85 | 60 |  | 0 | [21 empty] | Tchws | Tcws | 44 | 85 | 54 | 40 | 85 | 60 | 1.0347 | 1.085 | 0.75801 | Max/MinVar switch to get Max/MinOut
|  |  |  | Chlr | EIR_fTempCrvRef | Water-Cooled Centrifuga, Path B, >600ton | WtrCentPathBGtEql600ton | SI | E+ |  | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Temperature Curve | ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI | BiQuadratic | EIRRatio | Tchws | Tcws |  |  |  | 0.73762 | 0.001456 | -0.00022291 | 0.0071158 | 0.00026698 | -0.00073451 | [5 empty] | 1.08 | 0.76 | 12.22 | 4.44 | 29.44 | 15.56 |  | 1 | CrvDblQuad "ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI" Coef1 = 0.737625 Coef2 = 0.001456 Coef3 = -0.000223 Coef4 = 0.007116 Coef5 = 0.000267 Coef6 = -0.000735 MaxOut = 1.080 MinOut = 0.760 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 .. | CrvDblQuad "ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI" Coef1 = 0.737625 Coef2 = 0.001456 Coef3 = -0.000223 Coef4 = 0.007116 Coef5 = 0.000267 Coef6 = -0.000735 | MaxOut = 1.080 MinOut = 0.760 MaxVar1 = 12.220 MinVar1 = 4.440 MaxVar2 = 29.440 MinVar2 = 15.560 | .. | CrvDblQuad |  | "ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI" |  | 0.737625 | 0.001456 | -0.000223 | 0.007116 | 0.000267 | -0.000735 |  | 1.080 | 0.760 | 12.220 | 4.440 | 29.440 | 15.560 | Tchws | Tcws | 6.6667 | 29.4444 | 12.2222 | 4.4444 | 29.4444 | 15.5556 | 1.0342 | 1.0846 | 0.75777 | Max/MinVar switch to get Max/MinOut
|  |  | Electric Chiller Cooling Efficiency Adjustment Curves | Chlr | EIR_fPLRCrvRef | Water-Cooled Pos Displacement, Path A, All Capacities | WtrPosDispPathAAll |  | DOE2, E+ | EIR-fPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.31096 | 0.32252 | 0.37274 | [9 empty] | 0.35 |  | 0.1 |  |  |  | 1 | CrvQuad "ChlrWtrPosDispPathAAllEIRRatio_fQRatio" Coef1 = 0.310965 Coef2 = 0.322519 Coef3 = 0.372745 MinOut = 0.350 MinVar1 = 0.100 .. | CrvQuad "ChlrWtrPosDispPathAAllEIRRatio_fQRatio" Coef1 = 0.310965 Coef2 = 0.322519 Coef3 = 0.372745 | MinOut = 0.350 MinVar1 = 0.100 | .. | CrvQuad |  | "ChlrWtrPosDispPathAAllEIRRatio_fQRatio" |  | 0.310965 | 0.322519 | 0.372745 | - | - | - |  | - | 0.350 | - | 0.100 | - | - | QRatio |  | 1 |  |  | 0.1 |  |  | 1.0062 |  | 0.34694
|  |  |  | Chlr | EIR_fPLRCrvRef | Water-Cooled Centrifugal, Path A, All Capacities | WtrCentPathAAll |  | DOE2, E+ | EIR-fPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrWtrCentPathAAllEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.22215 | 0.50316 | 0.2569 | [9 empty] | 0.28 |  | 0.1 |  |  |  | 1 | CrvQuad "ChlrWtrCentPathAAllEIRRatio_fQRatio" Coef1 = 0.222149 Coef2 = 0.503156 Coef3 = 0.256905 MinOut = 0.280 MinVar1 = 0.100 .. | CrvQuad "ChlrWtrCentPathAAllEIRRatio_fQRatio" Coef1 = 0.222149 Coef2 = 0.503156 Coef3 = 0.256905 | MinOut = 0.280 MinVar1 = 0.100 | .. | CrvQuad |  | "ChlrWtrCentPathAAllEIRRatio_fQRatio" |  | 0.222149 | 0.503156 | 0.256905 | - | - | - |  | - | 0.280 | - | 0.100 | - | - | QRatio |  | 1 |  |  | 0.1 |  |  | 0.98221 |  | 0.27503
|  |  |  | Chlr | EIR_fPLRCrvRef | Water-Cooled Positive Displacement, Path B, All Capacities | WtrPosDispPathBAll |  | DOE2, E+ | EIR-fPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrWtrPosDispPathBAllEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0 | 0.6206 | 0.3893 | [9 empty] | 0.07 |  | 0.1 |  |  |  | 1 | CrvQuad "ChlrWtrPosDispPathBAllEIRRatio_fQRatio" Coef1 = 0.000000 Coef2 = 0.620600 Coef3 = 0.389300 MinOut = 0.070 MinVar1 = 0.100 .. | CrvQuad "ChlrWtrPosDispPathBAllEIRRatio_fQRatio" Coef1 = 0.000000 Coef2 = 0.620600 Coef3 = 0.389300 | MinOut = 0.070 MinVar1 = 0.100 | .. | CrvQuad |  | "ChlrWtrPosDispPathBAllEIRRatio_fQRatio" |  | 0.000000 | 0.620600 | 0.389300 | - | - | - |  | - | 0.070 | - | 0.100 | - | - | QRatio |  | 1 |  |  | 0.1 |  |  | 1.0099 |  | 0.065953
|  |  |  | Chlr | EIR_fPLRCrvRef | Water-Cooled Centrifugal, Path B, <300ton | WtrCentPathBLt300ton |  | DOE2, E+ | EIR-fPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrWtrCentPathBLt300tonEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.20839 | -0.1214 | 0.91845 | [9 empty] | 0.21 |  | 0.1 |  |  |  | 1 | CrvQuad "ChlrWtrCentPathBLt300tonEIRRatio_fQRatio" Coef1 = 0.208389 Coef2 = -0.121404 Coef3 = 0.918455 MinOut = 0.210 MinVar1 = 0.100 .. | CrvQuad "ChlrWtrCentPathBLt300tonEIRRatio_fQRatio" Coef1 = 0.208389 Coef2 = -0.121404 Coef3 = 0.918455 | MinOut = 0.210 MinVar1 = 0.100 | .. | CrvQuad |  | "ChlrWtrCentPathBLt300tonEIRRatio_fQRatio" |  | 0.208389 | -0.121404 | 0.918455 | - | - | - |  | - | 0.210 | - | 0.100 | - | - | QRatio |  | 1 |  |  | 0.1 |  |  | 1.0054 |  | 0.20543
|  |  |  | Chlr | EIR_fPLRCrvRef | Water-Cooled Centrifugal, Path B, 300-600ton | WtrCentPathBGtEql300Lt600ton |  | DOE2, E+ | EIR-fPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.055483 | 0.45187 | 0.48824 | [9 empty] | 0.11 |  | 0.1 |  |  |  | 1 | CrvQuad "ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio" Coef1 = 0.055483 Coef2 = 0.451866 Coef3 = 0.488242 MinOut = 0.110 MinVar1 = 0.100 .. | CrvQuad "ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio" Coef1 = 0.055483 Coef2 = 0.451866 Coef3 = 0.488242 | MinOut = 0.110 MinVar1 = 0.100 | .. | CrvQuad |  | "ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio" |  | 0.055483 | 0.451866 | 0.488242 | - | - | - |  | - | 0.110 | - | 0.100 | - | - | QRatio |  | 1 |  |  | 0.1 |  |  | 0.99559 |  | 0.10555
|  |  |  | Chlr | EIR_fPLRCrvRef | Water-Cooled Centrifugal >600t. | WtrCentPathBGtEql600ton |  | DOE2, E+ | EIR-fPLR | Chiller:Electric:EIR | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio | Quadratic | EIRRatio | QRatio |  |  |  |  | 0.10743 | 0.15678 | 0.73934 | [9 empty] | 0.13 |  | 0.1 |  |  |  | 1 | CrvQuad "ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio" Coef1 = 0.107426 Coef2 = 0.156775 Coef3 = 0.739345 MinOut = 0.130 MinVar1 = 0.100 .. | CrvQuad "ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio" Coef1 = 0.107426 Coef2 = 0.156775 Coef3 = 0.739345 | MinOut = 0.130 MinVar1 = 0.100 | .. | CrvQuad |  | "ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio" |  | 0.107426 | 0.156775 | 0.739345 | - | - | - |  | - | 0.130 | - | 0.100 | - | - | QRatio |  | 1 |  |  | 0.1 |  |  | 1.0035 |  | 0.1305
|  |  | Electric Chiller Cooling Efficiency Adjustment Curves | Chlr | EIR_fPLRTempCrvRef | Water-Cooled Pos Displacement, Path A, All Capacities | WtrPosDispPathAAll | IP | DOE2 | EIR-fPLR&dT |  |  | ChlrWtrPosDispPathAAllEIRRatio_fQRatioDelTIP | BiQuadratic | EIRRatio | QRatio | DelT |  |  |  | 0.2768 | 0.27037 | 0.37274 | 0.0048193 | -0.00015556 | 0.0026073 | [5 empty] | 0.96 | 0.37 | 1 | 0.15 | 41 | 16 |  | 0 | [21 empty] | QRatio | DelT | 1 | 41 | 1 | 0.15 | 41 | 16 | 0.96291 | 0.96291 | 0.36929
|  |  |  | Chlr | EIR_fPLRTempCrvRef | Water-Cooled Centrifugal, Path A, All Capacities | WtrCentPathAAll | IP | DOE2 | EIR-fPLR&dT |  |  | ChlrWtrCentPathAAllEIRRatio_fQRatioDelTIP | BiQuadratic | EIRRatio | QRatio | DelT |  |  |  | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301 | [5 empty] | 0.97 | 0.31 | 1 | 0.15 | 41 | 16 |  | 0 | [21 empty] | QRatio | DelT | 1 | 41 | 1 | 0.15 | 41 | 16 | 0.97378 | 0.97378 | 0.30765
|  |  |  | Chlr | EIR_fPLRTempCrvRef | Water-Cooled Positive Displacement, Path B, All Capacities | WtrPosDispPathBAll | IP | DOE2 | EIR-fPLR&dT |  |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatioDelTIP | BiQuadratic | EIRRatio | QRatio | DelT |  |  |  | -0.20121 | 1.0939 | 0.11129 | 0.0043863 | 5.4295e-08 | -0.0044603 | [5 empty] | 1 | 0.02 | 1 | 0.15 | 41 | 16 |  | 0 | [21 empty] | QRatio | DelT | 1 | 41 | 1 | 0.15 | 41 | 16 | 1.0011 | 1.0011 | 0.024875
|  |  |  | Chlr | EIR_fPLRTempCrvRef | Water-Cooled Centrifugal, Path B, <300ton | WtrCentPathBLt300ton | IP | DOE2 | EIR-fPLR&dT |  |  | ChlrWtrCentPathBLt300tonEIRRatio_fQRatioDelTIP | BiQuadratic | EIRRatio | QRatio | DelT |  |  |  | 0.0099221 | 0.054002 | 0.91845 | 0.010597 | -3.3669e-05 | -0.0087703 | [5 empty] | 1 | 0.18 | 1 | 0.15 | 41 | 16 |  | 0 | [21 empty] | QRatio | DelT | 1 | 41 | 1 | 0.15 | 41 | 16 | 1.0007 | 1.0007 | 0.17857
|  |  |  | Chlr | EIR_fPLRTempCrvRef | Water-Cooled Centrifugal, Path B, 300-600ton | WtrCentPathBGtEql300Lt600ton | IP | DOE2 | EIR-fPLR&dT |  |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatioDelTIP | BiQuadratic | EIRRatio | QRatio | DelT |  |  |  | -0.036012 | 0.55779 | 0.48824 | 0.0038291 | 3.7281e-05 | -0.0052963 | [5 empty] | 1.01 | 0.12 | 1 | 0.15 | 41 | 16 |  | 0 | [21 empty] | QRatio | DelT | 1 | 41 | 1 | 0.15 | 41 | 16 | 1.0125 | 1.0125 | 0.11674
|  |  |  | Chlr | EIR_fPLRTempCrvRef | Water-Cooled Centrifugal >600t. | WtrCentPathBGtEql600ton | IP | DOE2 | EIR-fPLR&dT |  |  | ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatioDelTIP | BiQuadratic | EIRRatio | QRatio | DelT |  |  |  | -0.089543 | 0.32091 | 0.73934 | 0.0095381 | 1.5517e-05 | -0.0082068 | [5 empty] | 1.05 | 0.11 | 1 | 0.15 | 41 | 16 |  | 0 | [21 empty] | QRatio | DelT | 1 | 41 | 1 | 0.15 | 41 | 16 | 1.0514 | 1.0514 | 0.11211
FUEL AND ABSORBTION CHILLERS | [12 empty] | - | [48 empty] | 0
| 5.8.2 | 5-154 | Fuel and Steam Chiller Cooling Capacity Adjustment Curves | Chlr | Cap_fTempCrvRef | Single Stage Absorption | AbsorbSglStg | IP | DOE2 | FSCH-CAP-FT |  |  | ChlrAbsorbSglStgQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.72341 | 0.079006 | 0.000897 | 0.025285 | 4.8e-05 | 0.000276 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | Cap_fCondTempCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirQRatio_fTcwsSI | Quadratic | QRatio | Tcws |  |  |  |  | 5.0197 | -0.21922 | 0.0028889 | [10 empty] | 34 | 10 |  |  |  | 1 | CrvQuad "ChlrAbsorbSglStgIndirQRatio_fTcwsSI" Coef1 = 5.019667 Coef2 = -0.219222 Coef3 = 0.002889 MaxVar1 = 34.000 MinVar1 = 10.000 .. | CrvQuad "ChlrAbsorbSglStgIndirQRatio_fTcwsSI" Coef1 = 5.019667 Coef2 = -0.219222 Coef3 = 0.002889 | MaxVar1 = 34.000 MinVar1 = 10.000 | .. | CrvQuad |  | "ChlrAbsorbSglStgIndirQRatio_fTcwsSI" |  | 5.019667 | -0.219222 | 0.002889 | - | - | - |  | - | - | 34.000 | 10.000 | - | - | Tcws | 0 | 1 | 41 | 1 | 0.15 | 41 | 16 | 4.8033 | 4.8033 | 4.9868
|  |  |  | Chlr | Cap_fEvapTempCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirQRatio_fTchwsSI | Quadratic | QRatio | Tchws |  |  |  |  | 0.69057 | 0.065571 | -0.00289 | [10 empty] | 10 | 4 |  |  |  | 1 | CrvQuad "ChlrAbsorbSglStgIndirQRatio_fTchwsSI" Coef1 = 0.690571 Coef2 = 0.065571 Coef3 = -0.002890 MaxVar1 = 10.000 MinVar1 = 4.000 .. | CrvQuad "ChlrAbsorbSglStgIndirQRatio_fTchwsSI" Coef1 = 0.690571 Coef2 = 0.065571 Coef3 = -0.002890 | MaxVar1 = 10.000 MinVar1 = 4.000 | .. | CrvQuad |  | "ChlrAbsorbSglStgIndirQRatio_fTchwsSI" |  | 0.690571 | 0.065571 | -0.002890 | - | - | - |  | - | - | 10.000 | 4.000 | - | - | Tchws | 0 | 1 | 41 | 1 | 0.15 | 41 | 16 | 0.75325 | 0.75325 | 0.70034
|  |  |  | Chlr | Cap_fGenTempCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirQRatio_fTgenSI | Cubic | QRatio | Tgen |  |  |  |  | 25.359 | -1.0452 | 0.014006 | -5.99e-05 | [9 empty] | 95 | 70 |  |  |  | 1 | CrvCubic "ChlrAbsorbSglStgIndirQRatio_fTgenSI" Coef1 = 25.359010 Coef2 = -1.045196 Coef3 = 0.014006 Coef4 = -0.000060 MaxVar1 = 95.000 MinVar1 = 70.000 .. | CrvCubic "ChlrAbsorbSglStgIndirQRatio_fTgenSI" Coef1 = 25.359010 Coef2 = -1.045196 Coef3 = 0.014006 Coef4 = -0.000060 | MaxVar1 = 95.000 MinVar1 = 70.000 | .. | CrvCubic |  | "ChlrAbsorbSglStgIndirQRatio_fTgenSI" |  | 25.359010 | -1.045196 | 0.014006 | -0.000060 | - | - |  | - | - | 95.000 | 70.000 | - | - | Tgen | 0 | 1 | 41 | 1 | 0.15 | 41 | 16 | 24.3254 | 24.3254 | 25.2016
|  |  |  | Chlr | Cap_fTempCrvRef | Double Stage Absorption | AbsorbDblStg | IP | DOE2 | FSCH-CAP-FT |  |  | ChlrAbsorbDblStgQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | -0.81604 | -0.038707 | 0.00045 | 0.071491 | -6.36e-05 | 3.12e-05 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | Cap_fTempCrvRef | Direct-Fired Absorption | AbsorbDirect | IP | DOE2 | FSCH-CAP-FT |  |  | ChlrAbsorbDirectQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | Cap_fTempCrvRef | Engine-Driven Chiller | EngDrvSpdAll | IP | DOE2 | FSCH-CAP-FT |  |  | ChlrEngDrvSpdAllQRatio_fTchwsTcwsIP | BiQuadratic | QRatio | Tchws | Tcws |  |  |  | 0.5736 | 0.01868 | 0 | -0.0046533 | 0 | 0 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
| 5.8.2 | 5-158 | Fuel and Steam Chiller Cooling Efficiency Adjustment Curves | Chlr | FIR_fPLRCrvRef | Single Stage Absorption | AbsorbSglStg |  | DOE2 | FSCH-FIR-FPLR |  |  | ChlrAbsorbSglStgFIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 0.098585 | 0.58385 | 0.56066 | -0.24309 | [14 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.098585
|  |  |  | Chlr | HIR_fPLRCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirHIRRatio_fQRatioSI | Cubic | HIRRatio | QRatio |  |  |  |  | 0.96753 | 1.0144 | -1.1664 | 0.50792 | [9 empty] | 1 | 0.15 |  |  |  | 1 | CrvCubic "ChlrAbsorbSglStgIndirHIRRatio_fQRatioSI" Coef1 = 0.967530 Coef2 = 1.014360 Coef3 = -1.166360 Coef4 = 0.507920 MaxVar1 = 1.000 MinVar1 = 0.150 .. | CrvCubic "ChlrAbsorbSglStgIndirHIRRatio_fQRatioSI" Coef1 = 0.967530 Coef2 = 1.014360 Coef3 = -1.166360 Coef4 = 0.507920 | MaxVar1 = 1.000 MinVar1 = 0.150 | .. | CrvCubic |  | "ChlrAbsorbSglStgIndirHIRRatio_fQRatioSI" |  | 0.967530 | 1.014360 | -1.166360 | 0.507920 | - | - |  | - | - | 1.000 | 0.150 | - | - | QRatio | 0 | 1 | 41 | 1 | 0.15 | 41 | 16 | 21.6403 | 21.6403 | 9.2202
|  |  |  | Chlr | FIR_fPLRCrvRef | Double Stage Absorption | AbsorbDblStg |  | DOE2 | FSCH-FIR-FPLR |  |  | ChlrAbsorbDblStgFIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 0.013994 | 1.2404 | -0.91488 | 0.66044 | [14 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.013994
|  |  |  | Chlr | FIR_fPLRCrvRef | Direct-Fired Absorption | AbsorbDirect |  | DOE2 | FSCH-FIR-FPLR |  |  | ChlrAbsorbDirectFIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 0.13551 | 0.61798 | 0.24651 | 0 | [14 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.13551
| 5.8.2 | 5-158 |  | Chlr | FIR_fPLRCrvRef | Engine-Driven, % Spd <= Min | EngDrvSpdLtEqlMin |  | DOE2 | FSCH-FIR-FPLR |  |  | ChlrEngDrvSpdLtEqlMinFIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 0.3802 | 2.3609 | 0 | 0 | [14 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 2.7411 |  | 0.3802
|  |  |  | Chlr | FIR_fPLRCrvRef | Engine-Driven, % Spd>Min % < 60% | EngDrvSpdGtMinLtEql60 |  | DOE2 | FSCH-FIR-FPLR |  |  | ChlrEngDrvSpdGtMinLtEql60FIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 1.1434 | 0.022889 | 0 | 0 | [14 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1.1662 |  | 1.1434
|  |  |  | Chlr | FIR_fPLRCrvRef | Engine-Driven, % Spd > 60% | EngDrvSpdGt60 |  | DOE2 | FSCH-FIR-FPLR |  |  | ChlrEngDrvSpdGt60FIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 1.3886 | -0.38861 | 0 | 0 | [14 empty] | 0 | [21 empty] | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 1.3886
| 5.8.2 | 5-158 |  | Chlr | FIR_fTempCrvRef | Single Stage Absorption | AbsorbSglStg | IP | DOE2 | FSCH-FIR-FT |  |  | ChlrAbsorbSglStgFIRRatio_fTchwsTcwsIP | BiQuadratic | FIRRatio | Tchws | Tcws |  |  |  | 0.65227 | 0 | 0 | -0.000545 | 5.5e-05 | 0 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | HIR_fCondTempCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirHIRRatio_fTcwsSI | Cubic | HIRRatio | Tcws |  |  |  |  | 0.71202 | -0.00478 | 0.000864 | -1.3e-05 | [9 empty] | 30 | 7 |  |  |  | 1 | CrvCubic "ChlrAbsorbSglStgIndirHIRRatio_fTcwsSI" Coef1 = 0.712019 Coef2 = -0.004780 Coef3 = 0.000864 Coef4 = -0.000013 MaxVar1 = 30.000 MinVar1 = 7.000 .. | CrvCubic "ChlrAbsorbSglStgIndirHIRRatio_fTcwsSI" Coef1 = 0.712019 Coef2 = -0.004780 Coef3 = 0.000864 Coef4 = -0.000013 | MaxVar1 = 30.000 MinVar1 = 7.000 | .. | CrvCubic |  | "ChlrAbsorbSglStgIndirHIRRatio_fTcwsSI" |  | 0.712019 | -0.004780 | 0.000864 | -0.000013 | - | - |  | - | - | 30.000 | 7.000 | - | - | Tcws | 0 | 1 | 41 | 1 | 0.15 | 41 | 16 | 0.70757 | 0.70757 | 0.71111
|  |  |  | Chlr | HIR_fEvapTempCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirHIRRatio_fTchwsSI | Cubic | HIRRatio | Tchws |  |  |  |  | 0.99557 | 0.046821 | -0.01099 | 0.000608 | [9 empty] | 10 | 4 |  |  |  | 1 | CrvCubic "ChlrAbsorbSglStgIndirHIRRatio_fTchwsSI" Coef1 = 0.995571 Coef2 = 0.046821 Coef3 = -0.010990 Coef4 = 0.000608 MaxVar1 = 10.000 MinVar1 = 4.000 .. | CrvCubic "ChlrAbsorbSglStgIndirHIRRatio_fTchwsSI" Coef1 = 0.995571 Coef2 = 0.046821 Coef3 = -0.010990 Coef4 = 0.000608 | MaxVar1 = 10.000 MinVar1 = 4.000 | .. | CrvCubic |  | "ChlrAbsorbSglStgIndirHIRRatio_fTchwsSI" |  | 0.995571 | 0.046821 | -0.010990 | 0.000608 | - | - |  | - | - | 10.000 | 4.000 | - | - | Tchws | 0 | 1 | 41 | 1 | 0.15 | 41 | 16 | 1.0563 | 1.0563 | 1.0121
|  |  |  | Chlr | FIR_fTempCrvRef | Double Stage Absorption | AbsorbDblStg | IP | DOE2 | FSCH-FIR-FT |  |  | ChlrAbsorbDblStgFIRRatio_fTchwsTcwsIP | BiQuadratic | FIRRatio | Tchws | Tcws |  |  |  | 1.6587 | 0 | 0 | -0.29 | 0.00025 | 0 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | NEEDS REVIEW | Direct-Fired Absorption | AbsorbDirect | IP | DOE2 | FSCH-FIR1-FT |  |  | ChlrAbsorbDirectFIR1Ratio_fTchwsIP | Quadratic | FIR1Ratio | Tchws |  |  |  |  | 4.4287 | -0.13299 | 0.0012533 | [15 empty] | 0 | [21 empty] | Tchws
|  |  |  | Chlr | NEEDS REVIEW | Direct-Fired Absorption | AbsorbDirect | IP | DOE2 | FSCH-FIR2-FT |  |  | ChlrAbsorbDirectFIR2Ratio_fTcwsIP | Quadratic | FIR2Ratio | Tcws |  |  |  |  | 0.86174 | -0.0070892 | 0.0010251 | [15 empty] | 0 | [21 empty] | Tcws
| 5.8.2 | 5-158 |  | Chlr | FIR_fTempCrvRef | Engine-Driven, % Spd <= Min | EngDrvSpdLtEqlMin | IP | DOE2 | FSCH-FIR-FT |  |  | ChlrEngDrvSpdLtEqlMinFIRRatio_fTchwsTcwsIP | BiQuadratic | FIRRatio | Tchws | Tcws |  |  |  | 1.0881 | 0.014106 | 0 | -0.0083391 | 0 | 0 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | FIR_fTempCrvRef | Engine-Driven, % Spd>Min % < 60% | EngDrvSpdGtMinLtEql60 | IP | DOE2 | FSCH-FIR-FT |  |  | ChlrEngDrvSpdGtMinLtEql60FIRRatio_fTchwsTcwsIP | BiQuadratic | FIRRatio | Tchws | Tcws |  |  |  | 1.2362 | 0.016892 | 0 | -0.011524 | 0 | 0 | [12 empty] | 0 | [21 empty] | Tchws | Tcws
|  |  |  | Chlr | FIR_fTempCrvRef | Engine-Driven, % Spd > 60% | EngDrvSpdGt60 | IP | DOE2 | FSCH-FIR-FT |  |  | ChlrEngDrvSpdGt60FIRRatio_fTchwsTcwsIP | BiQuadratic | FIRRatio | Tchws | Tcws |  |  |  | 1.2362 | 0.016892 | 0 | -0.011524 | 0 | 0
|  |  |  | Chlr | Elec_fPLRCrvRef | Indirect Fired Single Stage Absorption | AbsorbSglStgIndir | SI | E+ |  | Chiller:Absorption:Indirect |  | ChlrAbsorbSglStgIndirEIRRatio_fQRatioSI | Linear | EIRRatio | QRatio |  |  |  |  | 1 | 0 | [16 empty] | 1 | CrvLin "ChlrAbsorbSglStgIndirEIRRatio_fQRatioSI" Coef1 = 1.000000 Coef2 = 0.000000 .. | CrvLin "ChlrAbsorbSglStgIndirEIRRatio_fQRatioSI" Coef1 = 1.000000 Coef2 = 0.000000 |  | .. | CrvLin |  | "ChlrAbsorbSglStgIndirEIRRatio_fQRatioSI" |  | 1.000000 | 0.000000 | - | - | - | - |  | - | - | - | - | - | - | QRatio | 0
COOLING TOWERS | [12 empty] | -
| 5.8.3 | 5-159 | Cooling Tower Capacity Adjustment Curves | HtRej | Cap_fTempCrvRef | All towers | All | IP | DOE2 | CTWR-CAP |  |  | HtRejAllCFMRatio_fTrangeTapproachIP | BiQuadratic | CFMRatio | Trange | Tapproach |  |  |  | -2.2289 | 0.1668 | -0.014102 | 0.032223 | 0.1856 | 0.24252 | [12 empty] | 0 | [21 empty] | Trange | Tapproach
|  |  |  | HtRej | Cap_fTempCrvRef | All towers | All | IP | DOE2 | CTWR-CAP |  |  | HtRejAllGPMRatio_fCFMRatioToawbIP | BiQuadratic | GPMRatio | CFMRatio | Toawb |  |  |  | 0.60531 | -0.035545 | 0.0080408 | 0.028603 | 0.00024972 | 0.0049086 | [12 empty] | 0 | [21 empty] | CFMRatio | Toawb
|  |  |  | HtRej | Cap_fCoolToolsCrvRef | All towers, CoolTools performance | CoolToolsClgTowerCap | SI | E+ |  | CoolingTowerPerformance:CoolTools |  | HtRejCoolToolsClgTowerCap_fSI | CoolToolsCoolingTowerCurve | [6 empty] | See ACM for independents/dependents | [16 empty] | See ACM for independents/dependents | 0
| 5.8.3 | 5-161 | Cooling Tower Power Adjustment Curve | HtRej | Pwr_fPLRCrvRef | All towers, variable speed fan | VSDFan |  | DOE2, E+ | CTWR-FAN-FPLR | Cooling Tower:VariableSpeed | Fan Power Ratio Function of Air Flow Rate Ratio Curve | HtRejVSDFanPwrRatio_fQRatio | Cubic | PwrRatio | QRatio |  |  |  |  | 0.33163 | -0.88568 | 0.60557 | 0.94848 | [14 empty] | 1 | CrvCubic "HtRejVSDFanPwrRatio_fQRatio" Coef1 = 0.331629 Coef2 = -0.885676 Coef3 = 0.605565 Coef4 = 0.948482 .. | CrvCubic "HtRejVSDFanPwrRatio_fQRatio" Coef1 = 0.331629 Coef2 = -0.885676 Coef3 = 0.605565 Coef4 = 0.948482 |  | .. | CrvCubic |  | "HtRejVSDFanPwrRatio_fQRatio" |  | 0.331629 | -0.885676 | 0.605565 | 0.948482 | - | - |  | - | - | - | - | - | - | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.33163
DEHUMIDIFICATION | [12 empty] | -
| 5.7.7.2 | 5-141 | Liquid Desiccant Performance Curves |  | NEEDS REVIEW |  |  |  | DOE2, E+ | Desc-T-FTW |  |  | - | BiQuadratic | Tdb | Tdb | W |  |  |  | 11.5335 | 0.65867 | -0.001028 | 0.29504 | -0.00017 | -0.0008724 | [11 empty] | Needs Review for compatibility with E+ | 0 | [21 empty] | Tdb | W
[5 empty] | NEEDS REVIEW |  |  |  | DOE2, E+ | Desc-W-FTW |  |  | - | BiQuadratic | W | Tdb | W |  |  |  | 11.8994 | -0.26956 | 0.0044549 | 0.083053 | 0.0006974 | 0.0015879 | [11 empty] | Needs Review for compatibility with E+ | 0 | [21 empty] | Tdb | W
[5 empty] | NEEDS REVIEW |  |  |  | DOE2, E+ | Desc-Gas-FTW |  |  | - | BiQuadratic | DescGas | Tdb | W |  |  |  | 58745.8008 | -1134.49 | -3.6676 | 3874.5901 | -1.6963 | -13.0732 | [11 empty] | Needs Review for compatibility with E+ | 0 | [21 empty] | Tdb | W
[5 empty] | NEEDS REVIEW |  |  |  | DOE2, E+ | Desc-kW-FTW |  |  | - | BiQuadratic | DesckW | Tdb | W |  |  |  | 3.5179 | -0.0059317 | 0 | 0.0040401 | 0 | 0 | [11 empty] | Needs Review for compatibility with E+ | 0 | [21 empty] | Tdb | W
WATER HEATERS | [12 empty] | -
| 5.9.1.2 |  | Fuel Water Heater Part Load Efficiency Curve | WtHtr | HIR_fPLRCrvRef | Gas-fired storage water heater | Stor |  | DOE2, E+ | ??? | WaterHeater:Mixed | Part Load Factor Curve Name | WtHtrStorFIRRatio_fQRatio | Cubic | FIRRatio | QRatio |  |  |  |  | 0.021826 | 0.97763 | 0.000543 | 0 | [7 empty] | 1 | 0.1 | 1 | 0.1 |  |  |  | 1 | CrvCubic "WtHtrStorFIRRatio_fQRatio" Coef1 = 0.021826 Coef2 = 0.977630 Coef3 = 0.000543 Coef4 = 0.000000 MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.100 .. | CrvCubic "WtHtrStorFIRRatio_fQRatio" Coef1 = 0.021826 Coef2 = 0.977630 Coef3 = 0.000543 Coef4 = 0.000000 | MaxOut = 1.000 MinOut = 0.100 MaxVar1 = 1.000 MinVar1 = 0.100 | .. | CrvCubic |  | "WtHtrStorFIRRatio_fQRatio" |  | 0.021826 | 0.977630 | 0.000543 | 0.000000 | - | - |  | 1.000 | 0.100 | 1.000 | 0.100 | - | - | QRatio |  | 1 |  |  | 0 |  |  | 1 |  | 0.021826
Note on AW14: David Reddy: Iterate to adequately separate Coef from curve name field
Note on K15: David Reddy: This needs to be reviewed closer and also compared to DOE-2.1
Note on BU125: Arent, John AEC: We should check with Taylor Engineering about this one, since they supplied the curves.
Note on BU131: Arent, John AEC: Check with Taylor Engineering -- not a very common curve.

## Sheet1
[7 empty] | CoilHtgHPQRatio_fToadbSI | Cubic | 0.72901 | 0.031927 | 0.0001364 | -8.748e-06
[7 empty] | CoilHtgHPEIRRatio_fToadbSI | Cubic | 1.2183 | -0.036117 | 0.0014204 | -2.6827e-05
|  |  | 1 | 2
|  |  | AirHP-Cap f(OADB) | AirHP-EIR f(OADB) |  | HP Performance, COP47-3.3
| 0 |  | CoilHtgHPQRatio_fToadbSI | CoilHtgHPEIRRatio_fToadbSI
| 1 |  | Cubic | Cubic
| 2 | a | 0.72901 | 1.2183
| 3 | b | 0.031927 | -0.036117
| 4 | c | 0.0001364 | 0.0014204
| 5 | d | -8.748e-06 | -2.6827e-05
| 6 | e | 0 | 0
| 7 | f | 0 | 0
OADB
| °F | °C |  |  | 3.3
| -11 | -23.8889 | 0.1634 | 3.2574 | 0.9871 | 1.0131
| -9 | -22.7778 | 0.17592 | 3.0949 | 0.93786 | 1.0663
| -7 | -21.6667 | 0.19026 | 2.9405 | 0.89106 | 1.1223
| -5 | -20.5556 | 0.20634 | 2.7939 | 0.84663 | 1.1812
| -3 | -19.4444 | 0.22408 | 2.6548 | 0.8045 | 1.243
| -1 | -18.3333 | 0.24342 | 2.5232 | 0.7646 | 1.3079
| 1 | -17.2222 | 0.26429 | 2.3987 | 0.72686 | 1.3758
| 3 | -16.1111 | 0.28661 | 2.2811 | 0.69123 | 1.4467
| 5 | -15 | 0.31031 | 2.1702 | 0.65763 | 1.5206
| 7 | -13.8889 | 0.33532 | 2.0658 | 0.626 | 1.5974
| 9 | -12.7778 | 0.36157 | 1.9677 | 0.59626 | 1.6771
| 11 | -11.6667 | 0.38898 | 1.8756 | 0.56836 | 1.7594
| 13 | -10.5556 | 0.41748 | 1.7893 | 0.54222 | 1.8443
| 15 | -9.4444 | 0.44701 | 1.7087 | 0.51779 | 1.9313
| 17 | -8.3333 | 0.47748 | 1.6334 | 0.49498 | 2.0203
| 19 | -7.2222 | 0.50883 | 1.5633 | 0.47374 | 2.1109
| 21 | -6.1111 | 0.54099 | 1.4982 | 0.45399 | 2.2027
| 23 | -5 | 0.57388 | 1.4377 | 0.43568 | 2.2953
| 25 | -3.8889 | 0.60742 | 1.3818 | 0.41873 | 2.3882
| 27 | -2.7778 | 0.64156 | 1.3302 | 0.40308 | 2.4809
| 29 | -1.6667 | 0.67622 | 1.2826 | 0.38865 | 2.573
| 31 | -0.55556 | 0.71132 | 1.2388 | 0.37539 | 2.6639
| 33 | 0.55556 | 0.74679 | 1.1987 | 0.36323 | 2.7531
| 35 | 1.6667 | 0.78256 | 1.1619 | 0.3521 | 2.8401
| 37 | 2.7778 | 0.81856 | 1.1283 | 0.34192 | 2.9246
| 39 | 3.8889 | 0.85472 | 1.0977 | 0.33265 | 3.0062
| 41 | 5 | 0.89096 | 1.0699 | 0.3242 | 3.0845
| 43 | 6.1111 | 0.92722 | 1.0445 | 0.31651 | 3.1594
| 45 | 7.2222 | 0.96342 | 1.0214 | 0.30952 | 3.2308
| 47 | 8.3333 | 0.99948 | 1.0004 | 0.30316 | 3.2986
^^ Insert Here

## TO DO
To Do:
To do:
LH | 2012-12-23 | Review Absorption and Engine Driven Chiller Requirements and Curves for compatibility with E+
LH | 2012-12-23 | Review Dehumidification curve compatibility with E+
LH | 2012-12-23 | Review and assign max/min inputs and outputs and for most curves
DR | 2013-05-13 | Update ACM section/page numbers

## Data Maps
Performance Maps Section
Some performance data is expressed not as a curve fit but as a performance map. The software can generate curve fits from this performance
data. The exact type of curve (polynomial, exponential) is left to the software developer, but the curve fit should have a high degree of accuracy
(R^2> 0.95 (exact metric to be determined), and curves that are normalized should produce an output of 1 +/- 0.005 with an input of 1.
Direct-Expansion Part-Load Efficiency Curves for Equipment without SEER Ratings
| EIR(PLR) | [6 empty] | PLF(PLR)
| PLR | EIR WSHP | EIR WS | EIR PTAC | EIR AS | EIR E+ |  | PLF WSHP | PLF WS | PLF PTAC | PLF AS | PLF E+
| 0 | 0.125 | 0.20123 | 0.125 | 0.20123 | 0 |  | 0 | 0 | 0 | 0 | 0.85
| 0.1 | 0.2125 | 0.21649 | 0.2125 | 0.21649 | 0.11561 |  | 0.47059 | 0.46191 | 0.47059 | 0.46191 | 0.865
| 0.2 | 0.3 | 0.26404 | 0.3 | 0.26404 | 0.22727 |  | 0.66667 | 0.75745 | 0.66667 | 0.75745 | 0.88
| 0.3 | 0.3875 | 0.33716 | 0.3875 | 0.33716 | 0.3352 |  | 0.77419 | 0.8898 | 0.77419 | 0.8898 | 0.895
| 0.4 | 0.475 | 0.42911 | 0.475 | 0.42911 | 0.43956 |  | 0.84211 | 0.93216 | 0.84211 | 0.93216 | 0.91
| 0.5 | 0.5625 | 0.53318 | 0.5625 | 0.53318 | 0.54054 |  | 0.88889 | 0.93777 | 0.88889 | 0.93777 | 0.925
| 0.6 | 0.65 | 0.64265 | 0.65 | 0.64265 | 0.6383 |  | 0.92308 | 0.93364 | 0.92308 | 0.93364 | 0.94
| 0.7 | 0.7375 | 0.75079 | 0.7375 | 0.75079 | 0.73298 |  | 0.94915 | 0.93236 | 0.94915 | 0.93236 | 0.955
| 0.8 | 0.825 | 0.85087 | 0.825 | 0.85087 | 0.82474 |  | 0.9697 | 0.94021 | 0.9697 | 0.94021 | 0.97
| 0.9 | 0.9125 | 0.93619 | 0.9125 | 0.93619 | 0.91371 |  | 0.9863 | 0.96135 | 0.9863 | 0.96135 | 0.985
| 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1
| For Air-Cooled DX with SEER Ratings, use EIR=PLR instead | [6 empty] | For Air-Cooled DX with SEER Ratings, use PLF=1 instead
| of the data map. | [6 empty] | of the data map.
Abbreviations:
WSHP - Water-Source Heat Pump
WS - Water-Source (Other)
PTAC - Packaged Terminal Air Conditioner
AS - Air-Source DX (Other)
Direct-Expansion Cooling Efficiency Curve for equipment with SEER Ratings
User Inputs: SEER, EER
| EWB | ODB | COOL-EIR-FT
| 67 | 95 | 1
| 57 | 82 | formula TBD
| 57 | 95 | formula TBD
| 57 | 110 | formula TBD
| 67 | 82 | EER/SEER
| 67 | 110 | formula TBD
| 77 | 82 | formula TBD
| 77 | 95 | formula TBD
| 77 | 110 | formula TBD
| Heat Pump Efficiency Adjustment Curve |  |  |  |  | Electric Heat Pump Heating Capacity Adjustment Curve
| User Inputs: COP17, COP47 |  |  |  |  | User Inputs: CAP17, CAP47
The two user inputs for these curves are Coefficient of Performance (COP) or Heating Capacity at 17F and 47F.
| Temp | EIR-FT |  |  |  | Temp | CAP-FT
| 67 | 0.856 |  |  |  | 67 | 1.337 | [5 empty] | = | (67,1.337)
| 57 | 0.919 |  |  |  | 57 | 1.175
| 47 | 1 |  |  |  | 47 | 1
| 17 | COP47/COP17 |  |  |  | 17 | CAP17/CAP47
| 7 | 1.266x COP47/COP17 |  |  |  | 7 | 0.702xCAP17/CAP47
| -13 | 3.428 |  |  |  | -13 | 0.153

## Abbreviations
Variable Abbreviations
| Variables | Description
| CFMRatio | Ratio of air flow (CFM) at part load to CFM at full load
| QRatio | Ratio of load (Q) output at part load to Q output at full load
| CoilBPF | Coil Bypass Factor (BPF)
| EIRRatio | Ratio of energy input ratio (EIR) at part load to EIR at full load
| FIRRatio | Ratio offuel input ratio (FIR) at part load to FIR at full load
| GPMRatio | Ratio of fluid flow (GPM) at part load to GPM at full load
| PwrRatio | Ratio of electrical power consumption at part load to power consumption at full load
| Tdb | Dry bulb temperature at object input
| Twb | Wet bulb temperature at object input
| Toadb | Outdoor air dry bulb temperature
| Toawb | Outdoor wet bulb temperature
| Trange | Cooling tower range temperature (difference between tower entering and leaving water temperatures)
| Tapproach | Cooling tower approach temperature (difference between tower leaving water and outdoor air wet-bulb temperatures)
| EffRatio | Ratio of effectiveness (Eff) at part load to effectiveness at full load
| DescGas | For dessicant systems, natural gas consumption
| DesckW | For dessicant systems, electricity consumption
| Win | Humidity ratio at object input
| Wout | Humidity ratio at object output
| Tchws | Chilled water supply temperature
| Tcws | Condenser water supply temperature
| DelT | For chillers only, difference between chilled water and condenser water supply temperatures
| TdbRatio | For E+ WSHP
| TwbRatio | For E+ WSHP
| TwtRatio | For E+ WSHP
| CFMRatio | For E+ WSHP
| GPMRatio | For E+ WSHP
Possible additional abbreviations
| Qop | Operating load
| Qav | Available load
| Qrtd | Rated load

## DX SEER Curves - Ref Only
SEER DX Performance Curve Results - SI Units
[13 empty] | 110 | 75
User input EER is defined, use that. Otherwise EER is calculated using ACM equation | [10 empty] | Tewb |  | Toadb
| EER | SEER |  |  | a | b | c | d | e | f | max x | min x | max y | min y | max f(x,y) | min f(x,y)
If EER is <13
| 11 | 13 | EER < 13, SEER < 15 | "CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI" | 0.68668 | -0.035826 | 0.00078066 | 0.025564 | 0.00016344 | -0.00055894 | 25 | 13.89 | 43.3333 | 23.8889 | 1.088 | 0.858
| 11 | 15 | EER < 13, SEER >= 15 | "CoilClgDXEER11SEER15EIRRatio_fTwbToadbSI" | -1.2471 | -0.027513 | 0.00075194 | 0.12112 | -0.0010126 | -0.00073578 | 25 | 13.89 | 43.3333 | 23.8889 | 1.085 | 0.587
| 11 | 17 | EER < 13, SEER >= 17 | "CoilClgDXEER11SEER17EIRRatio_fTwbToadbSI" | -2.7249 | -0.02112 | 0.00072997 | 0.19413 | -0.0019108 | -0.0008719 | 25 | 13.89 | 43.3333 | 23.8889 | 1.083 | 0.38
If EER is >=13
| 13 | 16 | EER >= 13, SEER < 18 | "CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI" | -0.19999 | -0.035686 | 0.00078656 | 0.074834 | -0.00051613 | -0.0005735 | 25 | 13.89 | 43.3333 | 23.8889 | 1.052 | 0.759
| 13 | 18 | EER >= 13, SEER >= 18 | "CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI" | -1.7905 | -0.028777 | 0.00076289 | 0.15339 | -0.0014824 | -0.00072065 | 25 | 13.89 | 43.3333 | 23.8889 | 1.049 | 0.536
| 13 | 20 | EER >= 13, SEER >= 20 | "CoilClgDXEER13SEER20EIRRatio_fTwbToadbSI" | -3.0605 | -0.023207 | 0.00074392 | 0.21609 | -0.0022534 | -0.00083941 | 25 | 13.89 | 43.3333 | 23.8889 | 1.047 | 0.358
Plot Comparisons
Entering air condition (Tewb)
|  |  | Tewb (F) | Tewb (C)
|  |  | 67 | 19.4444
Outdoor air condtions (Tdb)
|  |  | Tdb (F) | Tdb (C) | EER < 13, SEER < 15 | EER < 13, SEER >= 15 | EER < 13, SEER >= 17 | EER >= 13, SEER < 18 | EER >= 13, SEER >= 18 | EER >= 13, SEER >= 20
|  |  | 75 | 23.8889 | 0.72956 | 0.47607 | 0.28247 | 0.63027 | 0.42199 | 0.25581
|  |  | 85 | 29.4444 | 0.85962 | 0.76947 | 0.70062 | 0.83114 | 0.75706 | 0.69796
|  |  | 95 | 35 | 0.99978 | 1.0004 | 1.0008 | 1.0001 | 1.0006 | 1.001
|  |  | 105 | 40.5556 | 1.15 | 1.1688 | 1.1831 | 1.1373 | 1.1527 | 1.165
|  |  | 115 | 46.1111 | 1.3104 | 1.2747 | 1.2474 | 1.2426 | 1.2132 | 1.1898
Summary of curves used for v3c and earlier. Curve coefficients were switched between high and low EER groups. This has been corrected in v3d
|  |  | Average-Good SEER, EER>=13 | "CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI" | -0.199992 | -0.035686 | 0.000787 | 0.074834 | -0.000516 | -0.000573
|  |  | High SEER, EER>=13 | "CoilClgDXSEER15EER11EIRRatio_fTwbToadbSI" | -1.790474 | -0.028777 | 0.000763 | 0.153391 | -0.001482 | -0.000721
|  |  | Very high SEER, EER>=13 | "CoilClgDXSEER17EER11EIRRatio_fTwbToadbSI" | -3.060538 | -0.023207 | 0.000744 | 0.216093 | -0.002253 | -0.000839
|  |  | Std SEER, EER<13 | "CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI" | 0.686684 | -0.035826 | 0.000781 | 0.025564 | 0.000163 | -0.000559
|  |  | High SEER, EER<13 | "CoilClgDXSEER18EER13EIRRatio_fTwbToadbSI" | -1.247121 | -0.027513 | 0.000752 | 0.121123 | -0.001013 | -0.000736
|  |  | Very high SEER, EER<13 | "CoilClgDXSEER20EER13EIRRatio_fTwbToadbSI" | -2.724920 | -0.021120 | 0.000730 | 0.194128 | -0.001911 | -0.000872

## Chiller Curves - Ref Only
New Part-Load Curves
| PATH A | [8 empty] | PATH B
| Water Cooled Positive Displacement < 75 tons |  |  | Full load = | 0.78 | 0.63 |  |  |  | Water Cooled Positive Displacement < 75 tons |  |  | Full load = | 0.8 | IPLV = | 0.6
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | 0.4468 | 0.71399 | 0.2768 | [5 empty] | a | 0.33413 | 0.76681 | -0.20121
| b | 0.014742 | -0.0061933 | 0.27037 | [5 empty] | b | 0.021015 | -0.024317 | 1.0939
| c | 0.00013391 | 0.0001491 | 0.37274 | [5 empty] | c | -0.0001024 | 0.00026197 | 0.11129
| d | 0.00044024 | 0.0030655 | 0.0048193 | [5 empty] | d | -0.001407 | 0.0074109 | 0.0043863
| e | -1.5214e-05 | 0.00016787 | -0.00015556 | [5 empty] | e | -2.8516e-05 | 0.00011772 | 5.4295e-08
| f | -8.4707e-05 | -0.0002668 | 0.0026073 | [5 empty] | f | 7.0706e-05 | -0.00018203 | -0.0044603
| Water Cooled Positive Displacement > 75 tons & <150 tons |  |  | Full load = | 0.775 | IPLV = | 0.615 | Same as <75ton |  | Water Cooled Positive Displacement > 75 tons & <150 tons |  |  | Full load = | 0.79 | IPLV = | 0.586 | Same as <75ton
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | 0.4468 | 0.71399 | 0.2768 | [5 empty] | a | 0.33413 | 0.76681 | -0.20121
| b | 0.014742 | -0.0061933 | 0.27037 | [5 empty] | b | 0.021015 | -0.024317 | 1.0939
| c | 0.00013391 | 0.0001491 | 0.37274 | [5 empty] | c | -0.0001024 | 0.00026197 | 0.11129
| d | 0.00044024 | 0.0030655 | 0.0048193 | [5 empty] | d | -0.001407 | 0.0074109 | 0.0043863
| e | -1.5214e-05 | 0.00016787 | -0.00015556 | [5 empty] | e | -2.8516e-05 | 0.00011772 | 5.4295e-08
| f | -8.4707e-05 | -0.0002668 | 0.0026073 | [5 empty] | f | 7.0706e-05 | -0.00018203 | -0.0044603
| Water Cooled Positive Displacement >=150 & < 300 tons |  |  | Full load = | 0.68 | IPLV = | 0.58 | Same as <75ton |  | Water Cooled Positive Displacement >=150 & < 300 tons |  |  | Full load = | 0.718 | IPLV = | 0.54 | Same as <75ton
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | 0.4468 | 0.71399 | 0.2768 | [5 empty] | a | 0.33413 | 0.76681 | -0.20121
| b | 0.014742 | -0.0061933 | 0.27037 | [5 empty] | b | 0.021015 | -0.024317 | 1.0939
| c | 0.00013391 | 0.0001491 | 0.37274 | [5 empty] | c | -0.0001024 | 0.00026197 | 0.11129
| d | 0.00044024 | 0.0030655 | 0.0048193 | [5 empty] | d | -0.001407 | 0.0074109 | 0.0043863
| e | -1.5214e-05 | 0.00016787 | -0.00015556 | [5 empty] | e | -2.8516e-05 | 0.00011772 | 5.4295e-08
| f | -8.4707e-05 | -0.0002668 | 0.0026073 | [5 empty] | f | 7.0706e-05 | -0.00018203 | -0.0044603
| Water Cooled Positive Displacement >=300 tons |  |  | Full load = | 0.62 | IPLV = | 0.54 | Same as <75ton |  | Water Cooled Positive Displacement >=300 tons |  |  | Full load = | 0.639 | IPLV = | 0.49 | Same as <75ton
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | 0.4468 | 0.71399 | 0.2768 | [5 empty] | a | 0.33413 | 0.76681 | -0.20121
| b | 0.014742 | -0.0061933 | 0.27037 | [5 empty] | b | 0.021015 | -0.024317 | 1.0939
| c | 0.00013391 | 0.0001491 | 0.37274 | [5 empty] | c | -0.0001024 | 0.00026197 | 0.11129
| d | 0.00044024 | 0.0030655 | 0.0048193 | [5 empty] | d | -0.001407 | 0.0074109 | 0.0043863
| e | -1.5214e-05 | 0.00016787 | -0.00015556 | [5 empty] | e | -2.8516e-05 | 0.00011772 | 5.4295e-08
| f | -8.4707e-05 | -0.0002668 | 0.0026073 | [5 empty] | f | 7.0706e-05 | -0.00018203 | -0.0044603
| Water Cooled Centrifugal <150 tons |  |  | Full load = | 0.634 | IPLV = | 0.596 |  |  | Water Cooled Centrifugal <150 tons |  |  | Full load = | 0.639 | IPLV = | 0.45
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | -0.49737 | 1.1536 | 0.2797 | [5 empty] | a | 0.18098 | 0.87311 | 0.0099221
| b | -0.0095607 | -0.030679 | 0.57376 | [5 empty] | b | 0.031844 | -0.025208 | 0.054002
| c | -0.00059561 | 0.00030591 | 0.2569 | [5 empty] | c | -0.00015415 | 0.00036862 | 0.91845
| d | 0.043521 | 0.0067087 | -0.0058072 | [5 empty] | d | 0.0095659 | 0.018292 | 0.010597
| e | -0.00058394 | 5.28e-05 | 0.00014649 | [5 empty] | e | -0.00013547 | 4.7035e-05 | -3.3669e-05
| f | 0.00096007 | -9.297e-05 | -0.0035301 | [5 empty] | f | -5.3197e-05 | -0.00035766 | -0.0087703
| Water Cooled Centrifugal >=150 tons & < 300 tons |  |  | Full load = | 0.634 | IPLV = | 0.59558 | Same as <150ton |  | Water Cooled Centrifugal >=150 tons & < 300 tons |  |  | Full load = | 0.639 | IPLV = | 0.45 | Same as <150ton
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | -0.49737 | 1.1536 | 0.2797 | [5 empty] | a | 0.18098 | 0.87311 | 0.0099221
| b | -0.0095607 | -0.030679 | 0.57376 | [5 empty] | b | 0.031844 | -0.025208 | 0.054002
| c | -0.00059561 | 0.00030591 | 0.2569 | [5 empty] | c | -0.00015415 | 0.00036862 | 0.91845
| d | 0.043521 | 0.0067087 | -0.0058072 | [5 empty] | d | 0.0095659 | 0.018292 | 0.010597
| e | -0.00058394 | 5.28e-05 | 0.00014649 | [5 empty] | e | -0.00013547 | 4.7035e-05 | -3.3669e-05
| f | 0.00096007 | -9.297e-05 | -0.0035301 | [5 empty] | f | -5.3197e-05 | -0.00035766 | -0.0087703
| Water Cooled Centrifugal >=300 tons & < 600 tons |  |  | Full load = | 0.57605 | IPLV = | 0.54905 | Same as <150ton |  | Water Cooled Centrifugal >=300 tons & < 600 tons |  |  | Full load = | 0.6 | IPLV = | 0.4
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | -0.49737 | 1.1536 | 0.2797 | [5 empty] | a | 0.36396 | 0.97432 | -0.036012
| b | -0.0095607 | -0.030679 | 0.57376 | [5 empty] | b | 0.045022 | -0.0046317 | 0.55779
| c | -0.00059561 | 0.00030591 | 0.2569 | [5 empty] | c | -0.00027422 | 4.8004e-05 | 0.48824
| d | 0.043521 | 0.0067087 | -0.0058072 | [5 empty] | d | -0.002028 | -0.0020126 | 0.0038291
| e | -0.00058394 | 5.28e-05 | 0.00014649 | [5 empty] | e | -8.8275e-05 | 0.00015875 | 3.7281e-05
| f | 0.00096007 | -9.297e-05 | -0.0035301 | [5 empty] | f | -1.2166e-05 | -0.00021199 | -0.0052963
| Water Cooled Centrifugal >=600 tons |  |  | Full load = | 0.57 | IPLV = | 0.539 | Same as <150ton |  | Water Cooled Centrifugal >=600 tons |  |  | Full load = | 0.59 | IPLV = | 0.4
|  | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT | [6 empty] | Cap-fCHWT&ECT | EIR-fCHWT&ECT | EIR-fPLR&dT
| a | -0.49737 | 1.1536 | 0.2797 | [5 empty] | a | -0.4552 | 0.36702 | -0.089543
| b | -0.0095607 | -0.030679 | 0.57376 | [5 empty] | b | 0.031347 | 0.012466 | 0.32091
| c | -0.00059561 | 0.00030591 | 0.2569 | [5 empty] | c | -5.715e-05 | -6.8823e-05 | 0.73934
| d | 0.043521 | 0.0067087 | -0.0058072 | [5 empty] | d | 0.020383 | 0.005934 | 0.0095381
| e | -0.00058394 | 5.28e-05 | 0.00014649 | [5 empty] | e | -0.00015341 | 8.2447e-05 | 1.5517e-05
| f | 0.00096007 | -9.297e-05 | -0.0035301 | [5 empty] | f | -0.00012709 | -0.00022665 | -0.0082068
| Type | Category | Max kW/ton | Max IPLV | CurveName | CurveType | a | b | c | Checksum
| Path A | Water Cooled Positive Displacement < 75 tons | 0.78 | 0.63 | EIR-fPLR | Quadratic | 0.30006 | 0.33556 | 0.37274 | 1.0084
| Path A | Water Cooled Positive Displacement > 75 tons & <150 tons | 0.775 | 0.615 | EIR-fPLR | Quadratic | 0.30006 | 0.33556 | 0.37274 | 1.0084
| Path A | Water Cooled Positive Displacement >=150 & < 300 tons | 0.68 | 0.58 | EIR-fPLR | Quadratic | 0.30006 | 0.33556 | 0.37274 | 1.0084
| Path A | Water Cooled Positive Displacement >=300 tons | 0.62 | 0.54 | EIR-fPLR | Quadratic | 0.30006 | 0.33556 | 0.37274 | 1.0084
| Path A | Water Cooled Centrifugal <150 tons | 0.634 | 0.596 | EIR-fPLR | Quadratic | 0.22607 | 0.48551 | 0.2569 | 0.96848
| Path A | Water Cooled Centrifugal >=150 tons & < 300 tons | 0.634 | 0.596 | EIR-fPLR | Quadratic | 0.22607 | 0.48551 | 0.2569 | 0.96848
| Path A | Water Cooled Centrifugal >=300 tons & < 600 tons | 0.57605 | 0.549 | EIR-fPLR | Quadratic | 0.22607 | 0.48551 | 0.2569 | 0.96848
| Path A | Water Cooled Centrifugal >=600 tons | 0.57 | 0.539 | EIR-fPLR | Quadratic | 0.22607 | 0.48551 | 0.2569 | 0.96848
| Path B | Water Cooled Positive Displacement < 75 tons | 0.8 | 0.6 | EIR-fPLR | Quadratic | -0.091514 | 0.98241 | 0.11129 | 1.0022
| Path B | Water Cooled Positive Displacement > 75 tons & <150 tons | 0.79 | 0.586 | EIR-fPLR | Quadratic | -0.091514 | 0.98241 | 0.11129 | 1.0022
| Path B | Water Cooled Positive Displacement >=150 & < 300 tons | 0.718 | 0.54 | EIR-fPLR | Quadratic | -0.091514 | 0.98241 | 0.11129 | 1.0022
| Path B | Water Cooled Positive Displacement >=300 tons | 0.639 | 0.49 | EIR-fPLR | Quadratic | -0.091514 | 0.98241 | 0.11129 | 1.0022
| Path B | Water Cooled Centrifugal <150 tons | 0.639 | 0.45 | EIR-fPLR | Quadratic | 0.2538 | -0.16526 | 0.91845 | 1.007
| Path B | Water Cooled Centrifugal >=150 tons & < 300 tons | 0.639 | 0.45 | EIR-fPLR | Quadratic | 0.2538 | -0.16526 | 0.91845 | 1.007
| Path B | Water Cooled Centrifugal >=300 tons & < 600 tons | 0.6 | 0.4 | EIR-fPLR | Quadratic | 0.083017 | 0.42538 | 0.48824 | 0.99664
| Path B | Water Cooled Centrifugal >=600 tons | 0.59 | 0.4 | EIR-fPLR | Quadratic | 0.15861 | 0.11574 | 0.73934 | 1.0137
|  |  | Second Variable (dT) fixed at: |  | 25 | F
PATH A
|  | Taylor Curves: | a | b | c | d | e | f
|  |  | 0.2768 | 0.27037 | 0.37274 | 0.0048193 | -0.00015556 | 0.0026073
|  |  | 0.2768 | 0.27037 | 0.37274 | 0.0048193 | -0.00015556 | 0.0026073
|  |  | 0.2768 | 0.27037 | 0.37274 | 0.0048193 | -0.00015556 | 0.0026073
|  |  | 0.2768 | 0.27037 | 0.37274 | 0.0048193 | -0.00015556 | 0.0026073
|  |  | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
|  |  | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
|  |  | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
|  |  | 0.2797 | 0.57376 | 0.2569 | -0.0058072 | 0.00014649 | -0.0035301
Path B
|  |  | a | b | c | d | e | f
|  |  | -0.20121 | 1.0939 | 0.11129 | 0.0043863 | 5.4295e-08 | -0.0044603
|  |  | -0.20121 | 1.0939 | 0.11129 | 0.0043863 | 5.4295e-08 | -0.0044603
|  |  | -0.20121 | 1.0939 | 0.11129 | 0.0043863 | 5.4295e-08 | -0.0044603
|  |  | -0.20121 | 1.0939 | 0.11129 | 0.0043863 | 5.4295e-08 | -0.0044603
|  |  | 0.0099221 | 0.054002 | 0.91845 | 0.010597 | -3.3669e-05 | -0.0087703
|  |  | 0.0099221 | 0.054002 | 0.91845 | 0.010597 | -3.3669e-05 | -0.0087703
|  |  | -0.036012 | 0.55779 | 0.48824 | 0.0038291 | 3.7281e-05 | -0.0052963
|  |  | -0.089543 | 0.32091 | 0.73934 | 0.0095381 | 1.5517e-05 | -0.0082068

## Fan Curves - Ref Only
[13 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Curve #1 | Curve #2 | Curve #3 | Curve #4 | Curve #5 | Curve #6 | Curve #7 | Curve #8 |  |  | SDD Curve Name | FanAForBIPwrRatio_fCFMRatio | FanAForBIVanesPwrRatio_fCFMRatio | FanFCPwrRatio_fCFMRatio | FanFCVanesPwrRatio_fCFMRatio | FanVaneAxVpPwrRatio_fCFMRatio | FanVSDPwrRatio_fCFMRatio | FanVSD901PwrRatio_fCFMRatio
1 |  | AF or BI Riding the Curve | AF or BI inlet vanes | FC riding the curve | FC with inlet vanes | Vane-axial with variable pitch blades | Any fan with VSD | Any fan with VSD | VSD with static pressure reset |  |  | ACM Curve Name | AF or BI Riding the Curve | AF or BI inlet vanes | FC riding the curve | FC with inlet vanes | Vane-axial with variable pitch blades | Any fan with VSD | Any fan with VSD (90.1)
2 | Min | 0.7 | 0.87 | 0.5 | 0.5 | 0.4 | 0.1 | 0.1 | #N/A |  | 1 | MinOut | 0.7 | 0.87 | 0.5 | 0.5 | 0.4 | 0.1 | 0.1998
3 | Max | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A |  | 0 | MaxOut | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | a | 0.1631 | 0.9977 | 0.1224 | 0.3038 | 0.1639 | 0.070429 | 0.070429 | #N/A |  | 0 | a | 0.1631 | 0.9977 | 0.1224 | 0.3038 | 0.1639 | 0.070429 | 0.0013
5 | b | 1.5901 | -0.659 | 0.612 | -0.7608 | -0.4016 | 0.38533 | 0.38533 | #N/A |  | 1 | b | 1.5901 | -0.659 | 0.612 | -0.7608 | -0.4016 | 0.38533 | 0.147
6 | c | -0.8817 | 0.9547 | 0.5983 | 2.2729 | 1.9909 | -0.46086 | -0.46086 | #N/A |  | 2 | c | -0.8817 | 0.9547 | 0.5983 | 2.2729 | 1.9909 | -0.46086 | 0.9506
7 | d | 0.1281 | -0.2936 | -0.3334 | -0.8169 | -0.7541 | 1.0092 | 1.0092 | #N/A |  | 3 | d | 0.1281 | -0.2936 | -0.3334 | -0.8169 | -0.7541 | 1.0092 | -0.0998
| 0 | 0.7 | 0.9977 | 0.5 | 0.5 | 0.4 | 0.1 | 0.1 | #N/A | -42.53%
| 0.05 | 0.7 | 0.9671 | 0.5 | 0.5 | 0.4 | 0.1 | 0.1 | #N/A | -38.16%
| 0.1 | 0.7 | 0.94105 | 0.5 | 0.5 | 0.4 | 0.10536 | 0.10536 | #N/A | -34.44%
| 0.15 | 0.7 | 0.91934 | 0.5 | 0.5 | 0.4 | 0.12127 | 0.12127 | #N/A | -31.33%
| 0.2 | 0.7 | 0.90174 | 0.5 | 0.5 | 0.4 | 0.13713 | 0.13713 | #N/A | -28.82%
| 0.25 | 0.7 | 0.88803 | 0.5 | 0.5 | 0.4 | 0.15373 | 0.15373 | #N/A | -26.86%
| 0.3 | 0.7 | 0.878 | 0.5 | 0.5 | 0.4 | 0.1718 | 0.1718 | #N/A | -25.43%
| 0.35 | 0.7 | 0.87141 | 0.5 | 0.5 | 0.4 | 0.19211 | 0.19211 | #N/A | -24.49%
| 0.4 | 0.7 | 0.87 | 0.5 | 0.5 | 0.4 | 0.21541 | 0.21541 | #N/A | -24.29%
| 0.45 | 0.71177 | 0.87 | 0.5 | 0.5 | 0.4 | 0.24247 | 0.24247 | #N/A | -22.23%
| 0.5 | 0.75374 | 0.87018 | 0.5363 | 0.5 | 0.4 | 0.27403 | 0.27403 | #N/A | -15.45%
| 0.55 | 0.79225 | 0.8752 | 0.58452 | 0.5 | 0.4198 | 0.31086 | 0.31086 | #N/A | -10.47%
| 0.6 | 0.82742 | 0.88257 | 0.63297 | 0.5 | 0.47678 | 0.3537 | 0.3537 | #N/A | -6.666%
| 0.65 | 0.85933 | 0.89208 | 0.68142 | 0.54524 | 0.53692 | 0.40333 | 0.40333 | #N/A | -3.812%
| 0.7 | 0.88808 | 0.9035 | 0.72961 | 0.60476 | 0.59966 | 0.46049 | 0.46049 | #N/A | -1.737%
| 0.75 | 0.91376 | 0.91661 | 0.77729 | 0.66708 | 0.66445 | 0.52595 | 0.52595 | #N/A | -0.3114%
| 0.8 | 0.93648 | 0.93118 | 0.82421 | 0.73156 | 0.7307 | 0.60045 | 0.60045 | #N/A | 0.5654%
| 0.85 | 0.95633 | 0.94701 | 0.87012 | 0.79761 | 0.79785 | 0.68476 | 0.68476 | #N/A | 0.9738%
| 0.9 | 0.9734 | 0.96387 | 0.91477 | 0.86461 | 0.86535 | 0.77964 | 0.77964 | #N/A | 0.9786%
| 0.95 | 0.98779 | 0.98154 | 0.95792 | 0.93194 | 0.93262 | 0.88583 | 0.88583 | #N/A | 0.6326%
| 1 | 0.9996 | 0.9998 | 0.9993 | 0.999 | 0.9991 | 1 | 1 | #N/A | -0.02001%

## Pump Curves - Ref Only
| a | b | c | d | GPMRatio | Power NoRst | Power Rst
PumpVSDNoRstPwrRatio_fGPMRatio | 0 | 0.5726 | -0.301 | 0.7347 | 1 | 1.0063 | 1.0059
PumpVSDRstPwrRatio_fGPMRatio | 0 | 0.0205 | 0.4101 | 0.5753 | 0.95 | 0.90223 | 0.88284
PumpVSDNoRstEPPwrRatio_fGPMRatio | 0.103 | -0.04 | 0.767 | 0.1679 | 0.9 | 0.80713 | 0.77002
PumpVSDRstEPPwrRatio_fGPMRatio | 0.0273 | -0.1317 | 0.6642 | 0.4445 | 0.85 | 0.72044 | 0.66703
[5 empty] | 0.8 | 0.64161 | 0.57342
[5 empty] | 0.75 | 0.57009 | 0.48876
[5 empty] | 0.7 | 0.50533 | 0.41263
[5 empty] | 0.65 | 0.44678 | 0.34458
[5 empty] | 0.6 | 0.3939 | 0.2842
[5 empty] | 0.55 | 0.34611 | 0.23105
[5 empty] | 0.5 | 0.30289 | 0.18469
[5 empty] | 0.45 | 0.26367 | 0.14469
[5 empty] | 0.4 | 0.2279 | 0.11064
[5 empty] | 0.35 | 0.19504 | 0.082078
[5 empty] | 0.3 | 0.16453 | 0.058592
[5 empty] | 0.25 | 0.13582 | 0.039745
[5 empty] | 0.2 | 0.10836 | 0.025106
[5 empty] | 0.15 | 0.10836 | 0.025106
[5 empty] | 0.1 | 0.10836 | 0.025106
[5 empty] | 0.05 | 0.10836 | 0.025106
[5 empty] | 0 | 0.10836 | 0.025106

## E+ Reference
I/O = EnergyPlus Input/Output Reference, verison 10/6/12
Variables
[6 empty] | Dep. | Indep.
| I/O pg # | ERef pg # | Object Type: | Field | Eplus-Curve Type | Var1 | Var1 | Var2 | NOTES
FANS
| p.1368 | p. 767 | Fan:VariableVolume | Fan Power Coefficient 1-5 | Quartic | PwrRatio | CFMRatio |  | The constant coefficient (C1) in a fourth order polynomial curve giving the fraction of full load power (PLF) as a function of flow fraction (FF). Flow fraction is the air mass flow rate divided by the maximum air mass flow rate. The curve is: PLF = C1 + C2*FF + C3*FF2 + C4*FF3 + C5*FF4
PUMPS
| p. 1200 |  | Pump:Variable Speed | Coefficient 1-4 of the Part Load Performance Curve | Cubic | PwrRatio | GPMRatio |  | This numeric field contains the first coefficient in the part load ratio curve. The fraction of full load power is determined by the cubic equation: FractionFullLoadPower = C1+C2*PLR+C3*PLR^2+C4*PLR^5 where C1,C2,C3,and C4 are Coefficients 1 – 4 (below) and PLR is the Part Load Ratio.
COOLING COILS
| p.1241 |  | Coil:Cooling:DX:SingleSpeed | Total Cooling Capacity Function of Temperature Curve Name | BiQuadratic | QRatio | Twb | Toadb/Toawb | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the total cooling capacity as a function of the wet-bulb temperature of the air entering the cooling coil, and the dry-bulb temperature of the air entering the air-cooled condenser (wet-bulb temperature if modeling an evaporative-cooled condenser). The output of this curve is multiplied by the rated total cooling capacity to give the total cooling capacity at specific temperature operating conditions (i.e., at temperatures different from the rating point temperatures).
|  |  |  | Total Cooling Capacity Function of Flow Fraction Curve | Cubic | QRatio | CFMRatio |  | The name of a quadratic performance curve (ref: Performance Curves) that parameterizes the variation of total cooling capacity as a function of the ratio of actual air flow rate across the cooling coil to the rated air flow rate (i.e., fraction of full load flow). The output of this curve is multiplied by the rated total cooling capacity and the total cooling capacity modifier curve (function of temperature) to give the total cooling capacity at the specific temperature and air flow conditions at which the coil is operating. The curve is normalized to have the value of 1.0 when the actual air flow rate equals the rated air flow rate.
|  |  |  | Energy Input Ratio Function of Temperature Curve | BiQuadratic | EIRRatio | Twb | Toadb/Toawb | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the wet-bulb temperature of the air entering the cooling coil and the dry-bulb temperature of the air entering the air-cooled condenser (wet-bulb temperature if modeling an evaporative-cooled condenser). The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR (inverse of rated COP) to give the EIR at specific temperature operating conditions (i.e., at temperatures different from the rating point temperatures). The curve is normalized to a value of 1.0 at the rating point.
|  |  |  | Energy Input Ratio Function of Flow Fraction Curve | Quadratic Cubic | EIRRatio | CFMRatio |  | The name of a quadratic performance curve (Ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the ratio of actual air flow rate across the cooling coil to the rated air flow rate (i.e., fraction of full load flow). The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR and the EIR modifier curve (function of temperature) to give the EIR at the specific temperature and air flow conditions at which the cooling coil is operating. This curve is normalized to a value of 1.0 when the actual air flow rate equals the rated air flow rate. This curve is applied only at the high speed compressor, high speed fan operating point.
|  |  |  | Part Load Fraction Correlation Curve | Quadratic Cubic | EIRRatio | QRatio |  | This alpha field defines the name of a quadratic or cubic performance curve (Ref: Performance Curves) that parameterizes the variation of electrical power input to the DX unit as a function of the part load ratio (PLR, sensible cooling load/steady-state sensible cooling capacity). The product of the rated EIR and EIR modifier curves is divided by the output of this curve to give the “effective” EIR for a given simulation timestep. The part load fraction (PLF) correlation accounts for efficiency losses due to compressor cycling.
| p.1334 |  | Coil:Cooling:WaterToAirHeatPump:EquationFit | Total Cooling Capacity Coefficient 1 to 5 | QuadLinear | TotQRatio | TwbRatio, TwtRatio, CFMRatio, GPMRatio |  | These numeric fields contain the first to fifth coefficient for the heat pump power consumption. See: Tang,C. C. 2005. Modeling Packaged Heat Pumps in Quasi-Steady State Energy Simulation Program. M.S. Thesis. Department of Mechanical and Aerospace Engineering, Oklahoma State University. (downloadable from http://www.hvac.okstate.edu/)
|  |  |  | Sensible Cooling Capacity Coefficient 1 to 5 | QuintLinear (does not exist in E+) | SensQRatio | TdbRatio, TwbRatio, TwtRatio, CFMRatio, GPMRatio |  | These numeric fields contain the first to sixth coefficient for the heat pump sensible cooling capacity. See: Tang,C. C. 2005. Modeling Packaged Heat Pumps in Quasi-Steady State Energy Simulation Program. M.S. Thesis. Department of Mechanical and Aerospace Engineering, Oklahoma State University. (downloadable from http://www.hvac.okstate.edu/)
|  |  |  | Cooling Power Consumption Coefficient 1 to 5 | QuadLinear | PwrRatio | TwbRatio, TwtRatio, CFMRatio, GPMRatio |  | These numeric fields contain the first to fifth coefficient for the heat pump power consumption. See: Tang,C. C. 2005. Modeling Packaged Heat Pumps in Quasi-Steady State Energy Simulation Program. M.S. Thesis. Department of Mechanical and Aerospace Engineering, Oklahoma State University. (downloadable from http://www.hvac.okstate.edu/)
| p.1241 |  | Coil:Cooling:DX:TwoSpeed | Total Cooling Capacity Function of Temperature Curve Name | BiQuadratic | QRatio | Twb | Toadb/Toawb | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the total cooling capacity as a function of the wet-bulb temperature of the air entering the cooling coil, and the dry-bulb temperature of the air entering the air-cooled condenser (wet-bulb temperature if modeling an evaporative-cooled condenser). The output of this curve is multiplied by the rated total cooling capacity to give the total cooling capacity at specific temperature operating conditions (i.e., at temperatures different from the rating point temperatures). The curve is normalized to have the value of 1.0 at the rating point. This curve is used for performance at the high speed compressor, high speed fan operating point.
|  |  |  | Total Cooling Capacity Function of Flow Fraction Curve | Cubic | QRatio | CFMRatio |  | The name of a quadratic performance curve (ref: Performance Curves) that parameterizes the variation of total cooling capacity as a function of the ratio of actual air flow rate across the cooling coil to the rated air flow rate (i.e., fraction of full load flow). The output of this curve is multiplied by the rated total cooling capacity and the total cooling capacity modifier curve (function of temperature) to give the total cooling capacity at the specific temperature and air flow conditions at which the coil is operating. The curve is normalized to have the value of 1.0 when the actual air flow rate equals the rated air flow rate. This curve is applied only at the high speed compressor, high speed fan operating point. There is no corresponding curve for the low speed operating point.
|  |  |  | Energy Input Ratio Function of Temperature Curve | BiQuadratic | EIRRatio | Twb | Toadb/Toawb | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the wet-bulb temperature of the air entering the cooling coil and the dry-bulb temperature of the air entering the air-cooled condenser (wet-bulb temperature if modeling an evaporative-cooled condenser). The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR (inverse of rated COP) to give the EIR at specific temperature operating conditions (i.e., at temperatures different from the rating point temperatures). The curve is normalized to a value of 1.0 at the rating point. This curve is used for performance at the high speed compressor, high speed fan operating point.
|  |  |  | Energy Input Ratio Function of Flow Fraction Curve | Quadratic Cubic | EIRRatio | CFMRatio |  | The name of a quadratic performance curve (Ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the ratio of actual air flow rate across the cooling coil to the rated air flow rate (i.e., fraction of full load flow). The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR and the EIR modifier curve (function of temperature) to give the EIR at the specific temperature and air flow conditions at which the cooling coil is operating. This curve is normalized to a value of 1.0 when the actual air flow rate equals the rated air flow rate. This curve is applied only at the high speed compressor, high speed fan operating point. There is no corresponding curve for the low speed operating point.
|  |  |  | Part Load Fraction Correlation Curve | Quadratic Cubic | EIRRatio | QRatio |  | This alpha field defines the name of a quadratic or cubic performance curve (Ref: Performance Curves) that parameterizes the variation of electrical power input to the DX unit as a function of the part load ratio (PLR, sensible cooling load/steady-state sensible cooling capacity). The product of the rated EIR and EIR modifier curves is divided by the output of this curve to give the “effective” EIR for a given simulation timestep. The part load fraction (PLF) correlation accounts for efficiency losses due to compressor cycling.
|  |  |  | Low Speed Total Cooling Capacity Function of Temperature Curve Name | BiQuadratic | QRatio | Twb | Toadb/Toawb | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the total cooling capacity as a function of the wet-bulb temperature of the air entering the cooling coil, and the dry-bulb temperature of the air entering the air-cooled condenser (wet-bulb temperature if modeling an evaporative-cooled condenser). The output of this curve is multiplied by the rated total cooling capacity to give the total cooling capacity at specific temperature operating conditions (i.e., at temperatures different from the rating point temperatures). The curve is normalized to have the value of 1.0 at the rating point. This curve is used for performance at the low speed compressor, low speed fan operating point.
|  |  |  | Low Speed Energy Input Ratio Function of Temperature Curve Name | BiQuadratic | EIRRatio | Twb | Toadb/Toawb | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the wetbulb temperature of the air entering the cooling coil and the drybulb temperature of the air entering the air-cooled condenser (wetbulb temperature if modeling an evaporative-cooled condenser). The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR (inverse of rated COP) to give the EIR at specific temperature operating conditions (i.e., at temperatures different from the rating point temperatures). The curve is normalized to a value of 1.0 at the rating point. This curve is used for performance at the low speed compressor, low speed fan operating point.
HEATING COILS
| p. 1231 |  | Coil:Heating:Gas | Part Load Fraction Correlation Curve | Quadratic Cubic | FuelRatio | QRatio |  | This alpha field defines the name of a quadratic or cubic performance curve (Ref: Performance Curves) that parameterizes the variation of gas consumption rate by the heating coil as a function of the part load ratio (PLR, sensible heating load/nominal capacity of the heating coil). For any simulation timestep, the nominal gas consumption rate (heating load/burner efficiency) is divided by the part-load fraction (PLF) if a part-load curve has been defined. The part-load curve accounts for efficiency losses due to transient coil operation.
| p. 1285 |  | Coil:Heating:DX:SingleSpeed | Total Heating Capacity Function of Temperature Curve | BiQuadratic Quadratic Cubic | QRatio | Toadb | Tdb (optional) | This alpha field defines the name of a bi-quadratic, quadratic or cubic performance curve (ref: Performance Curves) that parameterizes the variation of the total heating capacity as a function of the both the indoor and outdoor air dry-bulb temperature or just the outdoor air dry-bulb temperature depending on the type of curve selected. The bi-quadratic curve is recommended if sufficient manufacturer data is available as it provides sensitivity to the indoor air dry-bulb temperature and a more realistic output. The output of this curve is multiplied by the rated total heating capacity to give the total heating capacity at specific temperature operating conditions (i.e., at an indoor air dry-bulb temperature or outdoor air dry-bulb temperature different from the rating point temperature). The curve is normalized to have the value of 1.0 at the rating point.
|  |  |  | Total Heating Capacity Function of Flow Fraction Curve | Quadratic Cubic |  |  |  | This alpha field defines the name of a quadratic or cubic performance curve (ref: Performance Curves) that parameterizes the variation of total heating capacity as a function of the ratio of actual air flow rate across the heating coil to the rated air flow rate (i.e., fraction of full load flow). The output of this curve is multiplied by the rated total heating capacity and the total heating capacity modifier curve (function of temperature) to give the total heating capacity at the specific temperature and air flow conditions at which the coil is operating. The curve is normalized to have the value of 1.0 when the actual air flow rate equals the rated air flow rate.
|  |  |  | Energy Input Ratio Function of Temperature Curve | BiQuadratic Quadratic Cubic |  |  |  | This alpha field defines the name of a bi-quadratic, quadratic or cubic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the both the indoor and outdoor air dry-bulb temperature or just the outdoor air dry-bulb temperature depending on the type of curve selected. The bi-quadratic curve is recommended if sufficient manufacturer data is available as it provides sensitivity to the indoor air dry-bulb temperature and a more realistic output. The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR (inverse of rated COP) to give the EIR at specific temperature operating conditions (i.e., at an indoor air dry-bulb temperature or outdoor air dry-bulb temperature different from the rating point temperature). The curve is normalized to have the value of 1.0 at the rating point.
|  |  |  | Energy Input Ratio Function of Flow Fraction Curve | Quadratic Cubic |  |  |  | This alpha field defines the name of a quadratic or cubic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the ratio of actual air flow rate across the heating coil to the rated air flow rate (i.e., fraction of full load flow). The EIR is the inverse of the COP. The output of this curve is multiplied by the rated EIR and the EIR modifier curve (function of temperature) to give the EIR at the specific temperature and air flow conditions at which the coil is operating. This curve is normalized to a value of 1.0 when the actual air flow rate equals the rated air flow rate.
|  |  |  | Part Load Fraction Correlation Curve | Quadratic Cubic |  |  |  | This alpha field defines the name of a quadratic or cubic performance curve (Ref: Performance Curves) that parameterizes the variation of electrical power input to the DX unit as a function of the part load ratio (PLR, sensible cooling load/steady-state sensible cooling capacity). The product of the rated EIR and EIR modifier curves is divided by the output of this curve to give the “effective” EIR for a given simulation timestep. The part load fraction (PLF) correlation accounts for efficiency losses due to compressor cycling. The part load fraction correlation should be normalized to a value of 1.0 when the part load ratio equals 1.0 (i.e., no efficiency losses when the compressor(s) run continuously for the simulation timestep).
|  |  |  | Defrost Energy Input Ratio Function of Temperature Curve | BiQuadratic |  |  |  | This alpha field defines the name of a bi-quadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) during reverse-cycle defrost periods as a function of the outdoor air dry-bulb temperature and the wet-bulb temperature of the air entering the indoor coil. The EIR is the inverse of the COP. The output of this curve is multiplied by the coil capacity, the fractional defrost time period and the runtime fraction of the heating coil to give the defrost power at the specific temperatures at which the indoor and outdoor coils are operating. This curve is only required when a reverse-cycle defrost strategy is selected. The curve is normalized to a value of 1.0 at the rating point conditions.
| p. 1348 |  | Coil:Heating:WaterToAirHeatPump:EquationFit | Heating Capacity Coefficient 1-5 | QuadLinear | QRatio | TwbRatio, TwtRatio, CFMRatio, GPMRatio |  | These numeric fields contain the first to fifth coefficient for the heat pump capacity.
|  |  |  | Heating Power Consumption Coefficient 1-5 | QuadLinear | PwrRatio |  |  | These numeric fields contain the first to fifth coefficient for the heat pump power consumption.
BOILERS
| pg. 597 |  | Boiler:HotWater | Normalized Boiler Efficiency Curve | Linear Quadratic Cubic BiQuadratic QuaraticLinear BiCubic | EffRatio | QRatio |  | This alpha field contains the curve name which describes the normalized heating efficiency (as a fraction of nominal thermal efficiency) of the boiler’s burner. If this field is left blank, the nominal thermal efficiency is assumed to be constant (i.e., Fuel Used is equal to the Theoretical Fuel Use in the equation above). When a boiler efficiency curve is used, the curve may be any valid curve object with 1 (PLR) or 2 (PLR and boiler outlet water temperature) independent variables. A tri-quadratic curve object is not allowed since it uses 3 independent variables. The linear, quadratic, and cubic curve types may be used when the boiler efficiency is soley a function of boiler part-load ratio (PLR). When this type of curve is used, the boiler should operate at (or very near) the design boiler water outlet temperature. Other curve types may be used when the boiler efficiency is a function of both PLR and boiler water temperature. Examples of valid single and dual independent variable equations are shown below. For all curve types PLR is always the x independent variable. When using 2 independent variables, the boiler outlet water temperature (Toutlet) is always the y independent variable.
| pg. 600 |  | Boiler:Steam | Coefficient 1, Coefficient 2, Coefficient 3 of Fuel Use Function of Part Load Ratio Curve | Quadratic | FuelRatio | QRatio |  | The steam boiler model provides a first order approximation of performance for fuel oil, gas and electric boilers. Boiler performance is based on a “theoretical” boiler efficiency (overall efficiency at design operating conditions) and a single quadratic fuel use/ part load ratio curve. This single curve accounts for all combustion inefficiencies and stack losses.
CHILLERS
| pg. 547 |  | Chiller:Electric | Capacity Ratio Curve | Quadratic | QRatio | DelT |  | Capacity Ratio Curve The Capacity Ratio Curve is a quadratic equation that determines the Ratio of Available Capacity to Nominal Capacity.
|  |  |  | Power Ratio Curve | Quadratic |  | QRatio |  | Power Ratio Curve The Power Ratio Curve is a quadratic equation that determines the Ratio of Full Load Power at Available Capacity to Full Load Power at Nominal Capacity.
|  |  |  | Full Load Ratio Curve |  |  |  |  | Full Load Ratio Curve The Full Load Ratio Curve is a quadratic equation that determines the fraction of full load power.
BiQuadratic
| pg. 553 |  | Chiller:Electric:EIR | Cooling Capacity Function of Temperature Curve | BiQuadratic |  |  |  | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the cooling capacity as a function of the leaving chilled water temperature and the entering condenser fluid temperature. The output of this curve is multiplied by the reference capacity to give the cooling capacity at specific temperature operating conditions (i.e., at temperatures different from the reference temperatures). The curve should have a value of 1.0 at the reference temperatures and flow rates specified above. The biquadratic curve should be valid for the range of water temperatures anticipated for the simulation.
|  |  |  | Electric Input to Cooling Output Ratio Function of Temperature Curve | BiQuadratic |  |  |  | The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input to cooling output ratio (EIR) as a function of the leaving chilled water temperature and the entering condenser fluid temperature. The EIR is the inverse of the COP. The output of this curve is multiplied by the reference EIR (inverse of the reference COP) to give the EIR at specific temperature operating conditions (i.e., at temperatures different from the reference temperatures). The curve should have a value of 1.0 at the reference temperatures and flow rates specified above. The biquadratic curve should be valid for the range of water temperatures anticipated for the simulation.
|  |  |  | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | Quadratic |  |  |  | The name of a quadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the part-load ratio (EIRfTPLR). The EIR is the inverse of the COP, and the part-load ratio is the actual cooling load divided by the chiller’s available cooling capacity. This curve is generated by dividing the operating electric input power by the available full-load capacity (do not divide by load) at the specific operating temperatures. The curve output should decrease from 1 towards 0 as part-load ratio decreases from 1 to 0. The output of this curve is multiplied by the reference full-load EIR (inverse of the reference COP) and the Energy Input to Cooling Output Ratio Function of Temperature Curve to give the EIR at the specific temperatures and part-load ratio at which the chiller is operating. This curve should have a value of 1.0 when the part-load ratio equals 1.0. An ideal chiller with the same efficiency at all part-load ratio’s would use a performance curve that has a value of 0 when the part-load ratio equals 0 (i.;e., a line connecting 0,0 and 1,1 when plotted as EIRfTPLR versus PLR), however, actual systems can have part-load EIR’s slightly above or below this line (i.e., part-load efficiency often differs from rated efficiency). The quadratic curve should be valid for the range of part-load ratios anticipated for the simulation.
| pg. 560 |  | Chiller:Electric:ReformulatedEIR | Cooling Capacity Function of Temperature Curve | BiQuadratic |  |  |  | Field: Cooling Capacity Function of Temperature Curve Name The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the cooling capacity as a function of the leaving chilled water temperature and the leaving condenser water temperature. The output of this curve is multiplied by the reference capacity to give the cooling capacity at specific temperature operating conditions (i.e., at temperatures different from the reference temperatures). The curve should have a value of 1.0 at the reference temperatures and flow rates specified above. The biquadratic curve should be valid for the range of water temperatures anticipated for the simulation (otherwise the program issues warning messages).
|  |  |  | Electric Input to Cooling Output Ratio Function of Temperature Curve | BiQuadratic |  |  |  | Field: Electric Input to Cooling Output Ratio Function of Temperature Curve Name The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input to cooling output ratio (EIR) as a function of the leaving chilled water temperature and the leaving condenser water temperature. The EIR is the inverse of the COP. The output of this curve is multiplied by the reference EIR (inverse of the reference COP) to give the EIR at specific temperature operating conditions (i.e., at temperatures different from the reference temperatures). The curve should have a value of 1.0 at the reference temperatures and flow rates specified above. The biquadratic curve should be valid for the range of water temperatures anticipated for the simulation (otherwise the program issues warning messages).
|  |  |  | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | BiCubic |  |  |  | Field: Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve Name The name of a bicubic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the leaving condenser water temperature and the part-load ratio (EIRfTPLR). The EIR is the inverse of the COP, and the part-load ratio is the actual cooling load divided by the chiller’s available cooling capacity. This curve is generated by dividing the operating electric input power by the available full-load capacity (do not divide by load) at the specific operating temperatures. The curve output should decrease from 1 towards 0 as part-load ratio decreases from 1 to 0. The output of this curve is multiplied by the reference full-load EIR (inverse of the reference COP) and the Energy Input to Cooling Output Ratio Function of Temperature Curve to give the EIR at the specific temperatures and part-load ratio at which the chiller is operating. This curve should have a value of 1.0 at the reference leaving condenser water temperature with the part-load ratio equal to 1.0. An ideal chiller with the same efficiency at all part-load ratio’s would use a performance curve that has a value of 0 when the part-load ratio equals 0 (i.;e., a line connecting 0,0 and 1,1 when plotted as EIRfTPLR versus PLR), however, actual systems can have part-load EIR’s slightly above or below this line (i.e., part-load efficiency often differs from rated efficiency). The bicubic curve should be valid for the range of condenser water temperatures and part-load ratios anticipated for the simulation (otherwise the program issues warning messages). Note: Although a bicubic curve requires 10 coefficients (ref. Curve:Bicubic), coefficients 7, 9 and 10 are typically not used in the performance curve described here and should be entered as 0 unless sufficient performance data and regression accuracy exist to justify the use of these coefficients. Additionally, coefficients 2, 3, and 6 should not be used unless sufficient temperature data is available to accurately define the performance curve (i.e., negative values may result from insufficient data).
ADDITIONAL CHILLERS
| pg. 535 |  | Chiller:Absorption | Generator Heat Input Part Load Ratio Curve | Quadratic |  |  |  | Generator Heat Input Part Load Ratio Curve The Generator Heat Input Part Load Ratio Curve is a quadratic equation that determines the Ratio of the generator load on the absorber to the demand on the chiller. The defining equation is: SteamInputRatio= C1/PLR+ C2+C3*PLR
|  |  |  | Pump Electric Use Part Load Ratio Curve | Quadratic |  |  |  | The Pump Electric Use Part Load Ratio Curve is a quadratic equation that determines the Ratio of the actual absorber pumping power to the nominal pumping power. The defining equation is: ElectricInputRatio=C1+C2*PLR+C3*PLR^2
|  |  | Chiller:Absorption:Indirect | Generator Heat Input Function of Part Load Ratio Curve | Quadratic Cubic |  |  |  | Field: Generator Heat Input Function of Part Load Ratio Curve Name This required alpha field specifies the name of the curve used to determine the heat input to the chiller. The curve is a quadratic or cubic curve which characterizes the heat input as a function of chiller part-load ratio. The curve output is multiplied by the chiller’s nominal capacity and operating part-load ratio or minimum part-load ratio, whichever is greater, to determine the amount of heat input required for the given operating conditons.
|  |  |  | Pump Electric Input Function of Part Load Ratio Curve | Quadratic Cubic |  |  |  | Field: Pump Electric Input Function of Part Load Ratio Curve Name This alpha field specifies the name of the curve used to determine the pump electrical input to the chiller. The curve is a quadratic or cubic curve which characterizes the pump electrical power as a function of chiller part-load ratio. The curve output is multiplied by the chiller’s nominal pumping power and operating part-load ratio or minimum part-load ratio, whichever is greater, to determine the amount of pumping power required for the given operating conditons.
|  |  |  | Capacity Correction Function of Condenser Temperature Curve | Quadratic Cubic |  |  |  | Field: Capacity Correction Function of Condenser Temperature Curve Name This alpha field specifies the name of a quadratic or cubic curve which correlates the chiller’s evaporator capacity as a function of condenser entering water temperature. This curve is used to correct nominal capacity at off-design condensing temperatures.
|  |  |  | Capacity Correction Function of Chilled Water Temperature | Quadratic Cubic |  |  |  | Field: Capacity Correction Function of Chilled Water Temperature Curve Name This alpha field specifies the name of a quadratic or cubic curve which correlates the chiller’s evaporator capacity as a function of evaporator leaving water temperature. This curve is used to correct nominal capacity at off-design evaporator temperatures.
|  |  |  | Capacity Correction Function of Generator Temperature Curve | Quadratic Cubic |  |  |  | Field: Capacity Correction Function of Generator Temperature Curve Name This alpha field specifies the name of a quadratic or cubic curve which correlates the chiller’s evaporator capacity as a function of generator entering water temperature. This curve is used to correct nominal capacity at off-design evaporator temperatures and is only used when the Generator Fluid Type is specified as Hot Water.
|  |  |  | Generator Heat Input Correction Function of Condenser Temperature Curve | Quadratic Cubic |  |  |  | Field: Generator Heat Input Correction Function of Condenser Temperature Curve Name This alpha field specifies the name of a quadratic or cubic curve which correlates the chiller’s heat input as a function of condenser entering water temperature. This curve is used to correct generator heat input at off-design condensing temperatures.
|  |  |  | Generator Heat Input Correction Function of Chilled Water Temperature Curve | Quadratic Cubic |  |  |  | Field: Generator Heat Input Correction Function of Chilled Water Temperature Curve Name This alpha field specifies the name of a quadratic or cubic curve which correlates the chiller’s heat input as a function of evaporator leaving water temperature. This curve is used to correct generator heat input at off-design evaporator temperatures.
| pg. 560 |  | Chiller:Electric:ReformulatedEIR | Cooling Capacity Function of Temperature Curve | BiQuadratic |  |  |  | Field: Cooling Capacity Function of Temperature Curve Name The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the cooling capacity as a function of the leaving chilled water temperature and the leaving condenser water temperature. The output of this curve is multiplied by the reference capacity to give the cooling capacity at specific temperature operating conditions (i.e., at temperatures different from the reference temperatures). The curve should have a value of 1.0 at the reference temperatures and flow rates specified above. The biquadratic curve should be valid for the range of water temperatures anticipated for the simulation (otherwise the program issues warning messages).
|  |  |  | Electric Input to Cooling Output Ratio Function of Temperature Curve | BiQuadratic |  |  |  | Field: Electric Input to Cooling Output Ratio Function of Temperature Curve Name The name of a biquadratic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input to cooling output ratio (EIR) as a function of the leaving chilled water temperature and the leaving condenser water temperature. The EIR is the inverse of the COP. The output of this curve is multiplied by the reference EIR (inverse of the reference COP) to give the EIR at specific temperature operating conditions (i.e., at temperatures different from the reference temperatures). The curve should have a value of 1.0 at the reference temperatures and flow rates specified above. The biquadratic curve should be valid for the range of water temperatures anticipated for the simulation (otherwise the program issues warning messages).
|  |  |  | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | BiCubic |  |  |  | Field: Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve Name The name of a bicubic performance curve (ref: Performance Curves) that parameterizes the variation of the energy input ratio (EIR) as a function of the leaving condenser water temperature and the part-load ratio (EIRfTPLR). The EIR is the inverse of the COP, and the part-load ratio is the actual cooling load divided by the chiller’s available cooling capacity. This curve is generated by dividing the operating electric input power by the available full-load capacity (do not divide by load) at the specific operating temperatures. The curve output should decrease from 1 towards 0 as part-load ratio decreases from 1 to 0. The output of this curve is multiplied by the reference full-load EIR (inverse of the reference COP) and the Energy Input to Cooling Output Ratio Function of Temperature Curve to give the EIR at the specific temperatures and part-load ratio at which the chiller is operating. This curve should have a value of 1.0 at the reference leaving condenser water temperature with the part-load ratio equal to 1.0. An ideal chiller with the same efficiency at all part-load ratio’s would use a performance curve that has a value of 0 when the part-load ratio equals 0 (i.;e., a line connecting 0,0 and 1,1 when plotted as EIRfTPLR versus PLR), however, actual systems can have part-load EIR’s slightly above or below this line (i.e., part-load efficiency often differs from rated efficiency). The bicubic curve should be valid for the range of condenser water temperatures and part-load ratios anticipated for the simulation (otherwise the program issues warning messages). Note: Although a bicubic curve requires 10 coefficients (ref. Curve:Bicubic), coefficients 7, 9 and 10 are typically not used in the performance curve described here and should be entered as 0 unless sufficient performance data and regression accuracy exist to justify the use of these coefficients. Additionally, coefficients 2, 3, and 6 should not be used unless sufficient temperature data is available to accurately define the performance curve (i.e., negative values may result from insufficient data).
| pg. 566 |  | Chiller:EngineDriven | Capacity Ratio Curve | Quadratic |  |  |  | Capacity Ratio Curve The Capacity Ratio Curve is a quadratic equation that determines the Ratio of Available Capacity to Nominal Capacity.
|  |  |  | Power Ratio Curve | Quadratic |  |  |  | Power Ratio Curve The Power Ratio Curve is a quadratic equation that determines the Ratio of Full Load to Power.
|  |  |  | Full Load Ratio Curve | Quadratic |  |  |  | Full Load Ratio Curve The Full Load Ratio Curve is a quadratic equation that determines the fraction of full load power.
|  |  |  | Fuel Use Curve | Quadratic |  |  |  | Field: Fuel Use Curve Name This alpha field contains the name of the Cooling Load to Fuel Use curve. The curve itself is specified separately using the EnergyPlus Curve Manager. The Fuel Use Curve is a quadratic equation that determines the ratio of Cooling Load to Fuel Energy. The defining equation is: CoolingLoadtoFuelCurve= C1+ C2*PLR+ C3*PLR^2 where PLR is the Part Load Ratio from the Chiller. The Part Load Based Fuel Input Curve determines the ratio of fuel energy per unit time (J/s) / cooling load (W).
|  |  |  | Jacket Heat Recovery Curve | Quadratic |  |  |  | Field: Jacket Heat Recovery Curve Name This alpha field contains the name of the Recovery Jacket Heat curve. The curve itself is specified separately using the EnergyPlus Curve Manager. The Recovery Jacket Heat Curve is a quadratic equation that determines the ratio of recovery jacket heat to fuel energy. The defining equation is: RecoveryJacketHeatToFuelRatio= C1+ C2RL+ C3RL^2 where RL is the Ratio of Load to Diesel Engine Capacity.
|  |  |  | Lube Heat Recovery Curve | Quadratic |  |  |  | Field: Lube Heat Recovery Curve Name This alpha field contains the name of the Recovery Lube Heat curve. The curve itself is specified separately using the EnergyPlus Curve Manager. The Recovery Lubricant Heat Curve is a quadratic equation that determines the ratio of recovery lube heat to fuel energy. The defining equation is: RecoveryLubeHeatToFuelRatio= C1+ C2RL+ C3RL^2 where RL is the Ratio of Load to Diesel Engine Capacity
|  |  |  | Total Exhaust Energy Curve | Quadratic |  |  |  | Field: Total Exhaust Energy Curve Name This alpha field contains the name of the Total Exhaust Energy curve. The curve itself is specified separately using the EnergyPlus Curve Manager. The Total Exhaust Energy Curve is a quadratic equation that determines the ratio of total exhaust energy to fuel energy. The defining equation is: TotalExhaustToFuelRatio= C1+ C2RL+ C3RL^2 where RL is the Ratio of Load to Diesel Engine Capacity
|  |  |  | Exhaust Temperature Curve | Quadratic |  |  |  | Field: Exhaust Temperature Curve Name This alpha field contains the name of the Exhaust Temperature curve. The curve itself is specified separately using the EnergyPlus Curve Manager. The Exhaust Temperature Curve is a quadratic equation that determines the absolute exhaust temperature. The defining equation is: AbsoluteExhaustTemperature=C1+ C2RL+ C3RL^2 where RL is the Ratio of Load to Diesel Engine Capacity
|  |  |  | U-Factor Times Area Curve |  |  |  |  | U-Factor Times Area Curve The U-Factor Times Area (UA) is an equation that determines the overall heat transfer coefficient for the exhaust gasses with the stack. The heat transfer coefficient ultimately helps determine the exhaust stack temperature. The defining equation is: UAToCapacityRatio= C1*EngineCapacity^C2
| pg. 573 |  | Chiller:CombustionTurbine
| pg. 581 |  | ChillerHeater:Absorption:DirectFired
| pg. 589 |  | ChillerHeater:Absorption:DoubleEffect
| pg. 686 |  | CoolingTower:VariableSpeed | Fan Power Ratio Function of Air Flow Rate Ratio Curve | Cubic |  |  |  | This alpha field contains the curve object name for fan power ratio (fan power/design fan power) as a function of air flow rate ratio (air flow rate/design air flow rate) [ref. Performance Curves]. The curve object must be a cubic curve and should be normalized to 1.0 at an air flow rate ratio of 1.0. If this field is left blank, a theoretical fan curve is assumed where fan power ratio is directly proportional to the air flow rate ratio cubed.
| pg. 691 |  | CoolingTowerPerformance:CoolTools | CoolToolsCrossFlow Curve |  |  |  |  | CoolingTowerPerformance:CoolTools Variable speed cooling towers can be modeled by EnergyPlus with user-selectable performance based on the CoolTools correlation, YorkCalc correlation, or user-defined coefficients for either the CoolTools or YorkCalc correlations. The empirical CoolTools tower correlation uses a set of 35 coefficients to model the thermal performance (approach temperature) of a cooling tower based on four independent variables. If the user specifies Model Type = CoolToolsCrossFlow in the CoolingTower:VariableSpeed object, then the 35 coefficients derived for the CoolTools simulation model are used and these coefficients are already defined within EnergyPlus.
| pg. 694 |  | CoolingTowerPerformance:YorkCalc
| NOTE: pg. 1475 |  | Evaporative Coolers | EvaporativeCooler:Direct:CelDekPad |  |  |  |  | Field: Direct Pad Area The face area of the evaporative pad in m2. With the area and mass flow rate, the air velocity is calculated and is used to determine the saturation efficiency. Field: Direct Pad Depth The depth of the evaporative pad in meters. The pad depth is used to determine the saturation efficiency.
| pg. 636 |  | WaterHeater:Mixed | Part Load Factor Curve Name | Quadratic Cubic |  | QRatio |  | The reference to the curve object that relates the overall efficiency of the water heater to the Runtime Fraction (if Control Type Cycle) or Part Load Ratio (if Control Type Modulate). This is an additional multiplier applied to the Heater Thermal Efficiency to compute fuel energy use. The Part Load Factor Curve should not have a value less than 0.1 in the domain from 0 to 1. If the Part Load Factor Curve accounts for ambient losses and/or parasitic fuel consumption, these effects should not also be input into the related fields in this object as that would result in double-counting.

## SDD Curve Name Proposal (hidden)
What SDD Object:Property(s) are relevant to this issue?
Curve reference (CurveRef) properties
Explanation of addition, revision, or clarification:
While auditing the ACM text and performance curve information, we noted that the term part-load-ratio "PLR" is used in a lot of different contexts, such as:
Fan Power: PLR is ratio of operating fan power (kW) to fan power at design conditions.
DX Coils: PLR is the ratio of operating cooling coil capacity (Btu/hr) to the maximum available coil capacity.
Pump Power: PLR is the ratio of operating pump flow rate (gpm) to the design flow rate.
To try and make the name of the SDD performance curves in library descriptive and consistent,we identified a list of descriptive abbreviations for independent and dependent variables, as well as the following naming scheme:
Variables | Description
CFMRatio | Ratio of air flow (CFM) at part load to CFM at full load
QRatio |  | Ratio of load (Q) output at part load to Q output at full load
CoilBPF |  | Coil Bypass Factor (BPF)
EIRRatio | Ratio of energy input ratio (EIR) at part load to EIR at full load
FIRRatio | Ratio offuel input ratio (FIR) at part load to FIR at full load
GPMRatio | Ratio of fluid flow (GPM) at part load to GPM at full load
PwrRatio | Ratio of electrical power consumption at part load to power consumption at full load
Tdb |  | Dry bulb temperature at object input
Twb |  | Wet bulb temperature at object input
Toadb |  | Outdoor air dry bulb temperature
Toawb |  | Outdoor wet bulb temperature
Trange |  | Cooling tower range temperature (difference between tower entering and leaving water temperatures)
Tapproach | Cooling tower approach temperature (difference between tower leaving water and outdoor air wet-bulb temperatures)
EffRatio | Ratio of effectiveness (Eff) at part load to effectiveness at full load
DescGas |  | For dessicant systems, natural gas consumption
DesckW |  | For dessicant systems, electricity consumption
Win |  | Humidity ratio at object input
Wout |  | Humidity ratio at object output
Tchws |  | Chilled water supply temperature
Tcws |  | Condenser water supply temperature
DelT |  | For chillers only, difference between chilled water and condenser water supply temperatures
The library curve naming scheme proposed is the concatenation of the following:
<SDD object name (shortform)> +
<Short unique string to identify the curve application> +
<Independent variable abbreviation (from above)> +
_f + <Dependent 1 variable abbreviation (from above)> +
_f + <Dependent 2 variable abbreviation (from above)> +
Examples:
CoilClgPTACQRatio_fTwb_fToadb
CoilClgPTACEIRRatio_fTwb_fToadb
ChlrWtrCentEIRRatio_fTchws_fTcws
ChlrAirScrollEIRRatio_fQRatio
Workbook that has the curve information and names is checked into Rules\Library folder