## Area Category Method
90.1 2010 Space Type | People | Sensible heat | Latent heat | Receptacle Load | Hot water | 90.1 2010 LPD | 90.1 2010 RCR Threshold | 90.1-2010 Ra | 90.1-2010 Rp | 90.1-2010 Exhaust | IMC 2012 Ra | IMC 2012 Rp | IMC 2012 Exhaust | T-24 2013 | Gas Equipment Power | Refrig Load | Illuminance Setpoint for Daylighting |  | Primary Sidelit Daylighting Zone Setpoint Adjustment Factor | Secondary Sidelit Daylighting Zone Setpoint Adjustment Factor | NACM Schedule
| # per 1000 ft² | per person | per person | W/ft² | Gal/h per person | W/ft2 |  | CFM/ft² | CFM/Person | CFM/ft2 | CFM/ft² | CFM/Person | CFM/ft2 | CFM/ft2 | Btu/h-ft2 | W/ft2 | Min (lux) | Max (lux)
Unoccupied-Exclude from Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied
Unoccupied-Include in Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied
Atrium - First 40 ft in height | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.03 | NotApplicable | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | ; | Note: LPD allowance is W/ft height
Atrium - Height above 40 ft | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.02 | NotApplicable | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail |  | Note: LPD allowance is W/ft height
Attic or Crawlspace (Naturally or Mechanically Ventilated) | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied
Attic or Crawlspace (Not Ventilated) | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied
Audience/Seating Area—Permanent - For auditorium | 142.8571 | 245 | 105 | 1 | 0.09 | 0.79 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly
Audience/Seating Area—Permanent - For Performing Arts Theater | 142.8571 | 245 | 105 | 0.5 | 0.09 | 2.43 | 8 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly
Audience/Seating Area—Permanent - For Motion Picture Theater | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.14 | 4 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly
Classroom/Lecture/Training | 50 | 245 | 155 | 1 | 0.18 | 1.24 | 4 | 0.12 | 10 | 0 | 10 | 0.12 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | School
Conference/Meeting/Multipurpose | 66.6667 | 245 | 155 | 1 | 0.09 | 1.23 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly
Copy Room | 10 | 250 | 250 | 0.2 | 0 | 0.69 | 10 | 0.5 | 0 | 0 | 5 | 0.06 | 0.5 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.66 | Width < 8 ft | 0.06 | 0 | 0 | 0 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Dining Area | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.65 | 4 | 0.18 | 7.5 | 0 | 7.5 | 0.18 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Dining Area - For Bar Lounge/Leisure Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 1.31 | 4 | 0.18 | 7.5 | 0 | 7.5 | 0.18 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Dining Area - For Family Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.89 | 4 | 0.18 | 7.5 | 0 | 7.5 | 0.18 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Dressing/Fitting Room for Performing Arts Theater | 20 | 255 | 475 | 0.5 | 0.578 | 0.4 | 6 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly
Electrical/Mechanical | 3 | 250 | 250 | 3 | 0 | 0.95 | 6 | 0 | 0 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse
Employee Breakroom | 66.6667 | 275 | 275 | 1 | 0.09 | 0.73 | 4 | 0.12 | 5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly
Food Preparation | 5 | 275 | 475 | 1.5 | 0.578 | 0.99 | 6 | 0.12 | 7.5 | 0 | 0 | 0 | 0.7 | 0.15 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant
Laboratory - For Classrooms | 10 | 250 | 200 | 2 | 0.18 | 1.28 | 6 | 0.18 | 10 | 0 | 10 | 0.18 | 1 | 0.15 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory
Laboratory - For Medical/Industrial/Research | 10 | 250 | 200 | 2 | 0.18 | 1.81 | 6 | 0.18 | 10 | 0 | 10 | 0.18 | 1 | 0.15 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory
Lobby | 10 | 250 | 250 | 0.5 | 0.09 | 0.9 | 4 | 0.06 | 5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Lobby - For Elevator | 10 | 250 | 250 | 0.5 | 0.09 | 0.64 | 6 | 0.06 | 5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Lobby - For Performing Arts Theater | 10 | 250 | 250 | 0.5 | 0.09 | 2 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Lobby - For Motion Picture Theater | 10 | 250 | 250 | 0.5 | 0.09 | 0.52 | 4 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Locker Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.75 | 6 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly
Lounge/Recreation | 66.6667 | 275 | 275 | 1 | 0.09 | 0.73 | 4 | 0.12 | 5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly
Office - Enclosed | 10 | 250 | 200 | 1.5 | 0.18 | 1.11 | 8 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office
Office - Open Plan | 10 | 250 | 200 | 1.5 | 0.18 | 0.98 | 4 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office
Restrooms | 10 | 250 | 250 | 0.2 | 0 | 0.98 | 8 | 0 | 0 | 50 cfm/toilet | 0 | 0 | 20/50f | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Sales Area (for accent lighting, see Section 9.6.2 (b)) | 33.3333 | 250 | 200 | 1 | 0.18 | 1.68 | 6 | 0.12 | 7.5 | 0 | 7.5 | 0.12 | 0 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail
Stairway | 10 | 250 | 250 | 0.2 | 0 | 0.69 | 10 | 0.06 | 0 | 0 | 0 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.63 | 6 | 0.06 | 5 | 0 | 0 | 0.12 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse
Workshop | 10 | 275 | 475 | 1 | 0.18 | 1.59 | 6 | 0.12 | 7.5 | 0 | 10 | 0.18 | 0.5 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing
Automotive - Service/Repair | 10 | 275 | 475 | 1 | 0.18 | 0.67 | 4 | 0.12 | 7.5 | 1.5 | 0 | 0 | 0.75 | 1.5 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing
Bank/Office - Banking Activity Area | 10 | 250 | 250 | 1.5 | 0.18 | 1.38 | 6 | 0.06 | 7.5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office
Convention Center - Audience Seating | 66.6667 | 245 | 155 | 1 | 0.09 | 0.82 | 4 | 0.06 | 5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly
Convention Center - Exhibit Space | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.45 | 4 | 0.06 | 7.5 | 0 | 10 | 0.06 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly
Courthouse/Police Station/Penitentiary - Courtroom | 10 | 250 | 200 | 1.5 | 0.18 | 1.72 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon
Courthouse/Police Station/Penitentiary - Confinement Cells | 10 | 250 | 250 | 0.5 | 0.192 | 1.1 | 6 | 0.12 | 5 | 0 | 5 | 0.12 | 1 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon
Courthouse/Police Station/Penitentiary - Judges’ Chambers | 10 | 250 | 200 | 1.5 | 0.18 | 1.17 | 8 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office
Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office
Courthouse/Police Station/Penitentiary - Penitentiary Classroom | 50 | 245 | 155 | 1 | 0.18 | 1.34 | 4 | 0.12 | 10 | 0 | 10 | 0.12 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | School
Courthouse/Police Station/Penitentiary - Penitentiary Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 1.07 | 6 | 0.18 | 7.5 | 0 | 7.5 | 0.18 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Dormitory - Living Quarters | 10 | 250 | 250 | 0.5 | 0.192 | 0.38 | 8 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon
Fire Stations - Engine Room | 3 | 250 | 250 | 3 | 0 | 0.56 | 4 | 0.75 | 0 | 0.75 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse
Fire Stations - Sleeping Quarters | 10 | 250 | 250 | 0.5 | 0.192 | 0.25 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon
Gymnasium/Fitness Center - Fitness Area 0.72 4 | 66.6667 | 255 | 875 | 0.5 | 0.18 | 0.72 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail
Gymnasium/Fitness Center - Gymnasium Audience Seating 0.43 6 | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 6 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office
Gymnasium/Fitness Center - Playing Area 1.20 4 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.2 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Hospital - Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.89 | Width < 8 ft | 0.06 | 0 | 0 | 0 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Hospital - Emergency | 10 | 250 | 200 | 1.5 | 0.24 | 2.26 | 6 | 0 | 15 | 0 | 30 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Exam/Treatment | 10 | 250 | 200 | 1.5 | 0.24 | 1.66 | 8 | 0 | 15 | 0 | 15 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Laundry/Washing | 10 | 250 | 250 | 3 | 0.18 | 0.6 | 4 | 0.12 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.3 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing
Hospital - Lounge/Recreation | 66.6667 | 275 | 275 | 1 | 0.09 | 1.07 | 6 | 0.06 | 5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly
Hospital - Medical Supply | 10 | 250 | 200 | 1.5 | 0.24 | 1.27 | 6 | 0.18 | 5 | 0 | 5 | 0.18 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Nursery | 10 | 250 | 200 | 1.5 | 0.24 | 0.88 | 6 | 0 | 0 | 0 | 15 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Nurses’ Station | 10 | 250 | 200 | 1.5 | 0.18 | 0.87 | 6 | 0.06 | 5 | 0 | 15 | 0 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office
Hospital - Operating Room | 10 | 250 | 200 | 1.5 | 0.24 | 1.89 | 6 | 0 | 30 | 0 | 30 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Patient Room | 10 | 250 | 200 | 1.5 | 0.24 | 0.62 | 6 | 0 | 25 | 0 | 25 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Pharmacy | 10 | 250 | 200 | 1.5 | 0.24 | 1.14 | 6 | 0.18 | 5 | 0 | 5 | 0.18 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Physical Therapy | 10 | 250 | 200 | 1.5 | 0.24 | 0.91 | 6 | 0 | 15 | 0 | 15 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Radiology/Imaging | 10 | 250 | 200 | 1.5 | 0.24 | 1.32 | 6 | 0 | 15 | 0 | 15 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hospital - Recovery | 10 | 250 | 200 | 1.5 | 0.24 | 1.15 | 6 | 0 | 15 | 0 | 15 | 0 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Hotel/Highway Lodging - Hotel Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.82 | 4 | 0.18 | 7.5 | 0 | 7.5 | 0.18 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Hotel/Highway Lodging - Hotel Guest Rooms | 5 | 245 | 155 | 0.5 | 4.48 | 1.11 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving
Hotel/Highway Lodging - Hotel Lobby | 10 | 250 | 250 | 0.5 | 0.18 | 1.06 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Hotel/Highway Lodging - Highway Lodging Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.88 | 4 | 0.18 | 7.5 | 0 | 7.5 | 0.18 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Hotel/Highway Lodging - Highway Lodging Guest Rooms | 5 | 245 | 155 | 0.5 | 4.48 | 0.75 | 6 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving
Library - Card File and Cataloging | 10 | 250 | 200 | 1.5 | 0.18 | 0.72 | 4 | 0.12 | 5 | 0 | 5 | 0.12 | 0 | 0.15 | 0 | 0 | 200 | 300 | 1 | 4 | Office
Library - Reading Area | 20 | 250 | 200 | 1.5 | 0.18 | 0.93 | 4 | 0.12 | 5 | 0 | 5 | 0.12 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office
Manufacturing - Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.41 | Width < 8 ft | 0.06 | 0 | 0 | 0 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Manufacturing - Detailed Manufacturing 1.29 4 | 10 | 250 | 200 | 1 | 0.18 | 1.29 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing
Manufacturing - Equipment Room 0.95 6 | 3 | 275 | 475 | 0.2 | 0.18 | 0.95 | 6 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse
Manufacturing - Extra High Bay (>50 ft Floor to Ceiling Height) | 10 | 275 | 475 | 1 | 0.18 | 1.05 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing
Manufacturing - High Bay (25–50 ft Floor to Ceiling Height) | 10 | 275 | 475 | 1 | 0.18 | 1.23 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing
Manufacturing - Low Bay (<25 ft Floor to Ceiling Ht) | 10 | 275 | 475 | 1 | 0.18 | 1.19 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing
Multifamily - Dwelling/Sleeping Units | 5 | 245 | 155 | 0.5 | 0 | As Designed | NotApplicable | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving
Museum - General Exhibition | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.05 | 6 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly
Museum - Restoration | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.02 | 6 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly
Parking Garage - Garage Area | 10 | 250 | 200 | 0 | 0 | 0.19 | 4 | 0.75 | 0 | 0.75 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking
Post Office - Sorting Area | 10 | 250 | 200 | 1 | 0.18 | 0.94 | 4 | 0.12 | 7.5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing
Religious Buildings - Audience Seating | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.53 | 4 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly
Religious Buildings - Fellowship Hall | 142.8571 | 245 | 105 | 0.5 | 0.09 | 0.64 | 4 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly
Religious Buildings - Worship Pulpit, Choir | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.53 | 4 | 0.06 | 5 | 0 | 5 | 0.06 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly
Retail - Dressing/Fitting Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.87 | 8 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly
Retail - Mall Concourse | 33.3333 | 250 | 250 | 0.5 | 0.18 | 1.1 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail
Retail - Sales Area (for accent lighting, see Section 9.6.3(c)) | 33.3333 | 250 | 200 | 1 | 0.18 | 1.68 | 6 | 0.12 | 7.5 | 0 | 7.5 | 0.12 | 0 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail
Sports Arena - Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office
Sports Arena - Court Sports Arena—Class 4 | 142.8571 | 245 | 105 | 1 | 0.09 | 0.72 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Sports Arena - Court Sports Arena—Class 3 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.2 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Sports Arena - Court Sports Arena—Class 2 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.92 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Sports Arena - Court Sports Arena—Class 1 | 142.8571 | 245 | 105 | 1 | 0.09 | 3.01 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Sports Arena - Ring Sports Arena | 142.8571 | 245 | 105 | 1 | 0.09 | 2.68 | 4 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Transportation - Air/Train/Bus—Baggage Area | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.76 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly
Transportation - Airport—Concourse | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.36 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail
Transportation - Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.54 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office
Transportation - Terminal—Ticket Counter | 33.3333 | 250 | 250 | 0.5 | 0.18 | 1.08 | 4 | 0.06 | 7.5 | 0 | 7.5 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly
Warehouse - Fine Material Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.95 | 6 | 0.06 | 10 | 0 | 0 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse
Warehouse - Medium/Bulky Material Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.58 | 4 | 0.06 | 10 | 0 | 0 | 0.06 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse

## App3-4A_SpaceBySpace-S901G_2010
// This table saved as App3-4A_SpaceBySpace-S901G_2010.csv | [17 empty] | IllumSetptMin
TABLE SpaceFunctionData
| FuncType | OccDens | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHtgRt | IntLPDReg | RCRThresh | S6212010_CodeVentPerArea | S6212010_CodeVentPerPerson | S6212010_CodeExhPerArea | IMC2012_CodeVentPerArea | IMC2012_CodeVentPerPerson | IMC2012_CodeExhPerArea | T24N2013_CodeVentPerArea | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef | ;
| //SpaceBySpace | # per 1000 ft² | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person | W/ft² |  | CFM/ft² | CFM/person | CFM/ft² | CFM/ft² | CFM/person | CFM/ft² | CFM/ft² | Btu/h-ft2 | W/ft2 | lux | lux |  |  |  | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule | ;
| Unoccupied-Exclude from Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Unoccupied-Include in Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Atrium - First 40 ft in height | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.03 | NotApplicable | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Atrium - Height above 40 ft | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.02 | NotApplicable | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Attic or Crawlspace (Naturally or Mechanically Ventilated) | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Attic or Crawlspace (Not Ventilated) | 0 | 250 | 250 | 0 | 0 | 0 | NotApplicable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Audience/Seating Area—Permanent - For auditorium | 142.8571 | 245 | 105 | 1 | 0.09 | 0.79 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Audience/Seating Area—Permanent - For Performing Arts Theater | 142.8571 | 245 | 105 | 0.5 | 0.09 | 2.43 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Audience/Seating Area—Permanent - For Motion Picture Theater | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.14 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Classroom/Lecture/Training | 50 | 245 | 155 | 1 | 0.18 | 1.24 | 4 | 0.12 | 10 | 0 | 0.12 | 10 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | ;
| Conference/Meeting/Multipurpose | 66.6667 | 245 | 155 | 1 | 0.09 | 1.23 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Copy Room | 10 | 250 | 250 | 0.2 | 0 | 0.69 | 10 | 0.5 | 0 | 0 | 0.06 | 5 | 0.5 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.66 | Width < 8 ft | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Dining Area | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.65 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dining Area - For Bar Lounge/Leisure Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 1.31 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dining Area - For Family Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.89 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dressing/Fitting Room for Performing Arts Theater | 20 | 255 | 475 | 0.5 | 0.578 | 0.4 | 6 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Electrical/Mechanical | 3 | 250 | 250 | 3 | 0 | 0.95 | 6 | 0 | 0 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Employee Breakroom | 66.6667 | 275 | 275 | 1 | 0.09 | 0.73 | 4 | 0.12 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Food Preparation | 5 | 275 | 475 | 1.5 | 0.578 | 0.99 | 6 | 0.12 | 7.5 | 0 | 0 | 0 | 0.7 | 0.15 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Laboratory - For Classrooms | 10 | 250 | 200 | 2 | 0.18 | 1.28 | 6 | 0.18 | 10 | 0 | 0.18 | 10 | 1 | 0.15 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LaboratoryOccupancy | LaboratoryReceptacle | LaboratoryServiceHotWater | LaboratoryLights | LaboratoryGasEquip | LaboratoryRefrigeration | LaboratoryInfiltration | LaboratoryHVACAvail | LaboratoryHtgSetpt | LaboratoryClgSetpt | LaboratoryElevator | LaboratoryEscalator | LaboratoryWtrHtrSetpt | ;
| Laboratory - For Medical/Industrial/Research | 10 | 250 | 200 | 2 | 0.18 | 1.81 | 6 | 0.18 | 10 | 0 | 0.18 | 10 | 1 | 0.15 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LaboratoryOccupancy | LaboratoryReceptacle | LaboratoryServiceHotWater | LaboratoryLights | LaboratoryGasEquip | LaboratoryRefrigeration | LaboratoryInfiltration | LaboratoryHVACAvail | LaboratoryHtgSetpt | LaboratoryClgSetpt | LaboratoryElevator | LaboratoryEscalator | LaboratoryWtrHtrSetpt | ;
| Lobby | 10 | 250 | 250 | 0.5 | 0.09 | 0.9 | 4 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby - For Elevator | 10 | 250 | 250 | 0.5 | 0.09 | 0.64 | 6 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby - For Performing Arts Theater | 10 | 250 | 250 | 0.5 | 0.09 | 2 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby - For Motion Picture Theater | 10 | 250 | 250 | 0.5 | 0.09 | 0.52 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Locker Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.75 | 6 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lounge/Recreation | 66.6667 | 275 | 275 | 1 | 0.09 | 0.73 | 4 | 0.12 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Office - Enclosed | 10 | 250 | 200 | 1.5 | 0.18 | 1.11 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Office - Open Plan | 10 | 250 | 200 | 1.5 | 0.18 | 0.98 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Restrooms | 10 | 250 | 250 | 0.2 | 0 | 0.98 | 8 | 0 | 0 | 50 cfm/toilet | 0 | 0 | 20/50f | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Sales Area (for accent lighting, see Section 9.6.2 (b)) | 33.3333 | 250 | 200 | 1 | 0.18 | 1.68 | 6 | 0.12 | 7.5 | 0 | 0.12 | 7.5 | 0 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Stairway | 10 | 250 | 250 | 0.2 | 0 | 0.69 | 10 | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.63 | 6 | 0.06 | 5 | 0 | 0.12 | 0 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Workshop | 10 | 275 | 475 | 1 | 0.18 | 1.59 | 6 | 0.12 | 7.5 | 0 | 0.18 | 10 | 0.5 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Automotive - Service/Repair | 10 | 275 | 475 | 1 | 0.18 | 0.67 | 4 | 0.12 | 7.5 | 1.5 | 0 | 0 | 0.75 | 1.5 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Bank/Office - Banking Activity Area | 10 | 250 | 250 | 1.5 | 0.18 | 1.38 | 6 | 0.06 | 7.5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Convention Center - Audience Seating | 66.6667 | 245 | 155 | 1 | 0.09 | 0.82 | 4 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Convention Center - Exhibit Space | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.45 | 4 | 0.06 | 7.5 | 0 | 0.06 | 10 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Courtroom | 10 | 250 | 200 | 1.5 | 0.18 | 1.72 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Confinement Cells | 10 | 250 | 250 | 0.5 | 0.192 | 1.1 | 6 | 0.12 | 5 | 0 | 0.12 | 5 | 1 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Judges’ Chambers | 10 | 250 | 200 | 1.5 | 0.18 | 1.17 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Penitentiary Classroom | 50 | 245 | 155 | 1 | 0.18 | 1.34 | 4 | 0.12 | 10 | 0 | 0.12 | 10 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | ;
| Courthouse/Police Station/Penitentiary - Penitentiary Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 1.07 | 6 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dormitory - Living Quarters | 10 | 250 | 250 | 0.5 | 0.192 | 0.38 | 8 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Fire Stations - Engine Room | 3 | 250 | 250 | 3 | 0 | 0.56 | 4 | 0.75 | 0 | 0.75 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Fire Stations - Sleeping Quarters | 10 | 250 | 250 | 0.5 | 0.192 | 0.25 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Gymnasium/Fitness Center - Fitness Area 0.72 4 | 66.6667 | 255 | 875 | 0.5 | 0.18 | 0.72 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Gymnasium/Fitness Center - Gymnasium Audience Seating 0.43 6 | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 6 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Gymnasium/Fitness Center - Playing Area 1.20 4 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.2 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hospital - Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.89 | Width < 8 ft | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Hospital - Emergency | 10 | 250 | 200 | 1.5 | 0.24 | 2.26 | 6 | 0 | 15 | 0 | 0 | 30 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Exam/Treatment | 10 | 250 | 200 | 1.5 | 0.24 | 1.66 | 8 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Laundry/Washing | 10 | 250 | 250 | 3 | 0.18 | 0.6 | 4 | 0.12 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.3 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Hospital - Lounge/Recreation | 66.6667 | 275 | 275 | 1 | 0.09 | 1.07 | 6 | 0.06 | 5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hospital - Medical Supply | 10 | 250 | 200 | 1.5 | 0.24 | 1.27 | 6 | 0.18 | 5 | 0 | 0.18 | 5 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Nursery | 10 | 250 | 200 | 1.5 | 0.24 | 0.88 | 6 | 0 | 0 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Nurses’ Station | 10 | 250 | 200 | 1.5 | 0.18 | 0.87 | 6 | 0.06 | 5 | 0 | 0 | 15 | 0 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Hospital - Operating Room | 10 | 250 | 200 | 1.5 | 0.24 | 1.89 | 6 | 0 | 30 | 0 | 0 | 30 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Patient Room | 10 | 250 | 200 | 1.5 | 0.24 | 0.62 | 6 | 0 | 25 | 0 | 0 | 25 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Pharmacy | 10 | 250 | 200 | 1.5 | 0.24 | 1.14 | 6 | 0.18 | 5 | 0 | 0.18 | 5 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Physical Therapy | 10 | 250 | 200 | 1.5 | 0.24 | 0.91 | 6 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Radiology/Imaging | 10 | 250 | 200 | 1.5 | 0.24 | 1.32 | 6 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hospital - Recovery | 10 | 250 | 200 | 1.5 | 0.24 | 1.15 | 6 | 0 | 15 | 0 | 0 | 15 | 0 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Hotel/Highway Lodging - Hotel Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.82 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Hotel/Highway Lodging - Hotel Guest Rooms | 5 | 245 | 155 | 0.5 | 4.48 | 1.11 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Hotel/Highway Lodging - Hotel Lobby | 10 | 250 | 250 | 0.5 | 0.18 | 1.06 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hotel/Highway Lodging - Highway Lodging Dining | 66.6667 | 275 | 275 | 0.5 | 0.578 | 0.88 | 4 | 0.18 | 7.5 | 0 | 0.18 | 7.5 | 0 | 0.15 | 17.5377 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Hotel/Highway Lodging - Highway Lodging Guest Rooms | 5 | 245 | 155 | 0.5 | 4.48 | 0.75 | 6 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Library - Card File and Cataloging | 10 | 250 | 200 | 1.5 | 0.18 | 0.72 | 4 | 0.12 | 5 | 0 | 0.12 | 5 | 0 | 0.15 | 0 | 0 | 200 | 300 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Library - Reading Area | 20 | 250 | 200 | 1.5 | 0.18 | 0.93 | 4 | 0.12 | 5 | 0 | 0.12 | 5 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Manufacturing - Corridor/Transition | 10 | 250 | 250 | 0.2 | 0 | 0.41 | Width < 8 ft | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Manufacturing - Detailed Manufacturing 1.29 4 | 10 | 250 | 200 | 1 | 0.18 | 1.29 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Manufacturing - Equipment Room 0.95 6 | 3 | 275 | 475 | 0.2 | 0.18 | 0.95 | 6 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Manufacturing - Extra High Bay (>50 ft Floor to Ceiling Height) | 10 | 275 | 475 | 1 | 0.18 | 1.05 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Manufacturing - High Bay (25–50 ft Floor to Ceiling Height) | 10 | 275 | 475 | 1 | 0.18 | 1.23 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Manufacturing - Low Bay (<25 ft Floor to Ceiling Ht) | 10 | 275 | 475 | 1 | 0.18 | 1.19 | 4 | 0.18 | 10 | 0 | 0 | 0 | 0.75 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Multifamily - Dwelling/Sleeping Units | 5 | 245 | 155 | 0.5 | 0 | As Designed | NotApplicable | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Museum - General Exhibition | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.05 | 6 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Museum - Restoration | 66.6667 | 250 | 250 | 1.5 | 0.09 | 1.02 | 6 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Parking Garage - Garage Area | 10 | 250 | 200 | 0 | 0 | 0.19 | 4 | 0.75 | 0 | 0.75 | 0 | 0 | 0.75 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | ;
| Post Office - Sorting Area | 10 | 250 | 200 | 1 | 0.18 | 0.94 | 4 | 0.12 | 7.5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Religious Buildings - Audience Seating | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.53 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Religious Buildings - Fellowship Hall | 142.8571 | 245 | 105 | 0.5 | 0.09 | 0.64 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Religious Buildings - Worship Pulpit, Choir | 142.8571 | 245 | 105 | 0.5 | 0.09 | 1.53 | 4 | 0.06 | 5 | 0 | 0.06 | 5 | 0 | 0.15 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Retail - Dressing/Fitting Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.87 | 8 | 0.25 | 0 | 0.25 | 0 | 0 | 0.25 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Retail - Mall Concourse | 33.3333 | 250 | 250 | 0.5 | 0.18 | 1.1 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Retail - Sales Area (for accent lighting, see Section 9.6.3(c)) | 33.3333 | 250 | 200 | 1 | 0.18 | 1.68 | 6 | 0.12 | 7.5 | 0 | 0.12 | 7.5 | 0 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Sports Arena - Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.43 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 4 | 142.8571 | 245 | 105 | 1 | 0.09 | 0.72 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 3 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.2 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 2 | 142.8571 | 245 | 105 | 1 | 0.09 | 1.92 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Court Sports Arena—Class 1 | 142.8571 | 245 | 105 | 1 | 0.09 | 3.01 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Sports Arena - Ring Sports Arena | 142.8571 | 245 | 105 | 1 | 0.09 | 2.68 | 4 | 0.3 | 0 | 0 | 0.3 | 0 | 0 | 0.15 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Transportation - Air/Train/Bus—Baggage Area | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.76 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Transportation - Airport—Concourse | 33.3333 | 250 | 250 | 0.5 | 0.18 | 0.36 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Transportation - Audience Seating | 10 | 250 | 250 | 0.5 | 0.18 | 0.54 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Transportation - Terminal—Ticket Counter | 33.3333 | 250 | 250 | 0.5 | 0.18 | 1.08 | 4 | 0.06 | 7.5 | 0 | 0.06 | 7.5 | 0 | 0.15 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Warehouse - Fine Material Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.95 | 6 | 0.06 | 10 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Warehouse - Medium/Bulky Material Storage | 3 | 275 | 475 | 0.2 | 0.18 | 0.58 | 4 | 0.06 | 10 | 0 | 0.06 | 0 | 0 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
ENDTABLE
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
//
// | [22 empty] | Occupancy | Receptacle | ServiceHotWater | Lights | GasEquip | Refrigeration | Infiltration | HVACAvail | HtgSetpt | ClgSetpt | Elevator | Escalator | WtrHtrSetpt

## FuncSchGrp Table
// Schedule names by Space:FunctionScheduleGroup
TABLE SpaceFunctionGroups
| FuncGroup | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | ProcGasSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef
// | Function Group Name | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Process Gas Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule
| Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt
| Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt
| Laboratory | LaboratoryOccupancy | LaboratoryReceptacle | LaboratoryServiceHotWater | LaboratoryLights | LaboratoryGasEquip | LaboratoryRefrigeration | LaboratoryInfiltration | LaboratoryHVACAvail | LaboratoryHtgSetpt | LaboratoryClgSetpt | LaboratoryElevator | LaboratoryEscalator | LaboratoryWtrHtrSetpt
| Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt
| Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt
| ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt
| ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt
| Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt
| Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt
| School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt
ENDTABLE

## Enumerations-SpaceBySpace
// This List (column A) pasted into S901G_2010 BEMEnums.txt (after T24 enums list)
2, 0, "- specify -" | 2, | 0 | , | " | - specify - | "
2, 98, "Unoccupied-Exclude from Gross Floor Area" | 2, | 98 | , | " | Unoccupied-Exclude from Gross Floor Area | "
2, 99, "Unoccupied-Include in Gross Floor Area" | 2, | 99 | , | " | Unoccupied-Include in Gross Floor Area | "
2, 201, "Atrium - First 40 ft in height" | 2, | 201 | , | " | Atrium - First 40 ft in height | "
2, 202, "Atrium - Height above 40 ft" | 2, | 202 | , | " | Atrium - Height above 40 ft | "
2, 203, "Attic or Crawlspace (Naturally or Mechanically Ventilated)" | 2, | 203 | , | " | Attic or Crawlspace (Naturally or Mechanically Ventilated) | "
2, 204, "Attic or Crawlspace (Not Ventilated)" | 2, | 204 | , | " | Attic or Crawlspace (Not Ventilated) | "
2, 205, "Audience/Seating Area—Permanent - For auditorium" | 2, | 205 | , | " | Audience/Seating Area—Permanent - For auditorium | "
2, 206, "Audience/Seating Area—Permanent - For Performing Arts Theater" | 2, | 206 | , | " | Audience/Seating Area—Permanent - For Performing Arts Theater | "
2, 207, "Audience/Seating Area—Permanent - For Motion Picture Theater" | 2, | 207 | , | " | Audience/Seating Area—Permanent - For Motion Picture Theater | "
2, 208, "Classroom/Lecture/Training" | 2, | 208 | , | " | Classroom/Lecture/Training | "
2, 209, "Conference/Meeting/Multipurpose" | 2, | 209 | , | " | Conference/Meeting/Multipurpose | "
2, 210, "Corridor/Transition" | 2, | 210 | , | " | Corridor/Transition | "
2, 211, "Dining Area" | 2, | 211 | , | " | Dining Area | "
2, 212, "Dining Area - For Bar Lounge/Leisure Dining" | 2, | 212 | , | " | Dining Area - For Bar Lounge/Leisure Dining | "
2, 213, "Dining Area - For Family Dining" | 2, | 213 | , | " | Dining Area - For Family Dining | "
2, 214, "Dressing/Fitting Room for Performing Arts Theater" | 2, | 214 | , | " | Dressing/Fitting Room for Performing Arts Theater | "
2, 215, "Electrical/Mechanical" | 2, | 215 | , | " | Electrical/Mechanical | "
2, 216, "Food Preparation" | 2, | 216 | , | " | Food Preparation | "
2, 217, "Laboratory - For Classrooms" | 2, | 217 | , | " | Laboratory - For Classrooms | "
2, 218, "Laboratory - For Medical/Industrial/Research" | 2, | 218 | , | " | Laboratory - For Medical/Industrial/Research | "
2, 219, "Lobby" | 2, | 219 | , | " | Lobby | "
2, 220, "Lobby - For Elevator" | 2, | 220 | , | " | Lobby - For Elevator | "
2, 221, "Lobby - For Performing Arts Theater" | 2, | 221 | , | " | Lobby - For Performing Arts Theater | "
2, 222, "Lobby - For Motion Picture Theater" | 2, | 222 | , | " | Lobby - For Motion Picture Theater | "
2, 223, "Locker Room" | 2, | 223 | , | " | Locker Room | "
2, 224, "Lounge/Recreation" | 2, | 224 | , | " | Lounge/Recreation | "
2, 225, "Office - Enclosed" | 2, | 225 | , | " | Office - Enclosed | "
2, 226, "Office - Open Plan" | 2, | 226 | , | " | Office - Open Plan | "
2, 227, "Restrooms" | 2, | 227 | , | " | Restrooms | "
2, 228, "Sales Area (for accent lighting, see Section 9.6.2 (b))" | 2, | 228 | , | " | Sales Area (for accent lighting, see Section 9.6.2 (b)) | "
2, 229, "Stairway" | 2, | 229 | , | " | Stairway | "
2, 230, "Storage" | 2, | 230 | , | " | Storage | "
2, 231, "Workshop" | 2, | 231 | , | " | Workshop | "
2, 232, "Automotive - Service/Repair" | 2, | 232 | , | " | Automotive - Service/Repair | "
2, 233, "Bank/Office - Banking Activity Area" | 2, | 233 | , | " | Bank/Office - Banking Activity Area | "
2, 234, "Convention Center - Audience Seating" | 2, | 234 | , | " | Convention Center - Audience Seating | "
2, 235, "Convention Center - Exhibit Space" | 2, | 235 | , | " | Convention Center - Exhibit Space | "
2, 236, "Courthouse/Police Station/Penitentiary - Courtroom" | 2, | 236 | , | " | Courthouse/Police Station/Penitentiary - Courtroom | "
2, 237, "Courthouse/Police Station/Penitentiary - Confinement Cells" | 2, | 237 | , | " | Courthouse/Police Station/Penitentiary - Confinement Cells | "
2, 238, "Courthouse/Police Station/Penitentiary - Judges’ Chambers" | 2, | 238 | , | " | Courthouse/Police Station/Penitentiary - Judges’ Chambers | "
2, 239, "Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating" | 2, | 239 | , | " | Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | "
2, 240, "Courthouse/Police Station/Penitentiary - Penitentiary Classroom" | 2, | 240 | , | " | Courthouse/Police Station/Penitentiary - Penitentiary Classroom | "
2, 241, "Courthouse/Police Station/Penitentiary - Penitentiary Dining" | 2, | 241 | , | " | Courthouse/Police Station/Penitentiary - Penitentiary Dining | "
2, 242, "Dormitory - Living Quarters" | 2, | 242 | , | " | Dormitory - Living Quarters | "
2, 243, "Fire Stations - Engine Room" | 2, | 243 | , | " | Fire Stations - Engine Room | "
2, 244, "Fire Stations - Sleeping Quarters" | 2, | 244 | , | " | Fire Stations - Sleeping Quarters | "
2, 245, "Gymnasium/Fitness Center - Fitness Area 0.72 4" | 2, | 245 | , | " | Gymnasium/Fitness Center - Fitness Area 0.72 4 | "
2, 246, "Gymnasium/Fitness Center - Gymnasium Audience Seating 0.43 6" | 2, | 246 | , | " | Gymnasium/Fitness Center - Gymnasium Audience Seating 0.43 6 | "
2, 247, "Gymnasium/Fitness Center - Playing Area 1.20 4" | 2, | 247 | , | " | Gymnasium/Fitness Center - Playing Area 1.20 4 | "
2, 248, "Hospital - Corridor/Transition" | 2, | 248 | , | " | Hospital - Corridor/Transition | "
2, 249, "Hospital - Emergency" | 2, | 249 | , | " | Hospital - Emergency | "
2, 250, "Hospital - Exam/Treatment" | 2, | 250 | , | " | Hospital - Exam/Treatment | "
2, 251, "Hospital - Laundry/Washing" | 2, | 251 | , | " | Hospital - Laundry/Washing | "
2, 252, "Hospital - Lounge/Recreation" | 2, | 252 | , | " | Hospital - Lounge/Recreation | "
2, 253, "Hospital - Medical Supply" | 2, | 253 | , | " | Hospital - Medical Supply | "
2, 254, "Hospital - Nursery" | 2, | 254 | , | " | Hospital - Nursery | "
2, 255, "Hospital - Nurses’ Station" | 2, | 255 | , | " | Hospital - Nurses’ Station | "
2, 256, "Hospital - Operating Room" | 2, | 256 | , | " | Hospital - Operating Room | "
2, 257, "Hospital - Patient Room" | 2, | 257 | , | " | Hospital - Patient Room | "
2, 258, "Hospital - Pharmacy" | 2, | 258 | , | " | Hospital - Pharmacy | "
2, 259, "Hospital - Physical Therapy" | 2, | 259 | , | " | Hospital - Physical Therapy | "
2, 260, "Hospital - Radiology/Imaging" | 2, | 260 | , | " | Hospital - Radiology/Imaging | "
2, 261, "Hospital - Recovery" | 2, | 261 | , | " | Hospital - Recovery | "
2, 262, "Hotel/Highway Lodging - Hotel Dining" | 2, | 262 | , | " | Hotel/Highway Lodging - Hotel Dining | "
2, 263, "Hotel/Highway Lodging - Hotel Guest Rooms" | 2, | 263 | , | " | Hotel/Highway Lodging - Hotel Guest Rooms | "
2, 264, "Hotel/Highway Lodging - Hotel Lobby" | 2, | 264 | , | " | Hotel/Highway Lodging - Hotel Lobby | "
2, 265, "Hotel/Highway Lodging - Highway Lodging Dining" | 2, | 265 | , | " | Hotel/Highway Lodging - Highway Lodging Dining | "
2, 266, "Hotel/Highway Lodging - Highway Lodging Guest Rooms" | 2, | 266 | , | " | Hotel/Highway Lodging - Highway Lodging Guest Rooms | "
2, 267, "Library - Card File and Cataloging" | 2, | 267 | , | " | Library - Card File and Cataloging | "
2, 268, "Library - Reading Area" | 2, | 268 | , | " | Library - Reading Area | "
2, 269, "Manufacturing - Corridor/Transition" | 2, | 269 | , | " | Manufacturing - Corridor/Transition | "
2, 270, "Manufacturing - Detailed Manufacturing 1.29 4" | 2, | 270 | , | " | Manufacturing - Detailed Manufacturing 1.29 4 | "
2, 271, "Manufacturing - Equipment Room 0.95 6" | 2, | 271 | , | " | Manufacturing - Equipment Room 0.95 6 | "
2, 272, "Manufacturing - Extra High Bay (>50 ft Floor to Ceiling Height)" | 2, | 272 | , | " | Manufacturing - Extra High Bay (>50 ft Floor to Ceiling Height) | "
2, 273, "Manufacturing - High Bay (25–50 ft Floor to Ceiling Height)" | 2, | 273 | , | " | Manufacturing - High Bay (25–50 ft Floor to Ceiling Height) | "
2, 274, "Manufacturing - Low Bay (<25 ft Floor to Ceiling Ht)" | 2, | 274 | , | " | Manufacturing - Low Bay (<25 ft Floor to Ceiling Ht) | "
2, 275, "Multifamily - Dwelling/Sleeping Units" | 2, | 275 | , | " | Multifamily - Dwelling/Sleeping Units | "
2, 276, "Museum - General Exhibition" | 2, | 276 | , | " | Museum - General Exhibition | "
2, 277, "Museum - Restoration" | 2, | 277 | , | " | Museum - Restoration | "
2, 278, "Parking Garage - Garage Area" | 2, | 278 | , | " | Parking Garage - Garage Area | "
2, 279, "Post Office - Sorting Area" | 2, | 279 | , | " | Post Office - Sorting Area | "
2, 280, "Religious Buildings - Audience Seating" | 2, | 280 | , | " | Religious Buildings - Audience Seating | "
2, 281, "Religious Buildings - Fellowship Hall" | 2, | 281 | , | " | Religious Buildings - Fellowship Hall | "
2, 282, "Religious Buildings - Worship Pulpit, Choir" | 2, | 282 | , | " | Religious Buildings - Worship Pulpit, Choir | "
2, 283, "Retail - Dressing/Fitting Room" | 2, | 283 | , | " | Retail - Dressing/Fitting Room | "
2, 284, "Retail - Mall Concourse" | 2, | 284 | , | " | Retail - Mall Concourse | "
2, 285, "Retail - Sales Area (for accent lighting, see Section 9.6.3(c))" | 2, | 285 | , | " | Retail - Sales Area (for accent lighting, see Section 9.6.3(c)) | "
2, 286, "Sports Arena - Audience Seating" | 2, | 286 | , | " | Sports Arena - Audience Seating | "
2, 287, "Sports Arena - Court Sports Arena—Class 4" | 2, | 287 | , | " | Sports Arena - Court Sports Arena—Class 4 | "
2, 288, "Sports Arena - Court Sports Arena—Class 3" | 2, | 288 | , | " | Sports Arena - Court Sports Arena—Class 3 | "
2, 289, "Sports Arena - Court Sports Arena—Class 2" | 2, | 289 | , | " | Sports Arena - Court Sports Arena—Class 2 | "
2, 290, "Sports Arena - Court Sports Arena—Class 1" | 2, | 290 | , | " | Sports Arena - Court Sports Arena—Class 1 | "
2, 291, "Sports Arena - Ring Sports Arena" | 2, | 291 | , | " | Sports Arena - Ring Sports Arena | "
2, 292, "Transportation - Air/Train/Bus—Baggage Area" | 2, | 292 | , | " | Transportation - Air/Train/Bus—Baggage Area | "
2, 293, "Transportation - Airport—Concourse" | 2, | 293 | , | " | Transportation - Airport—Concourse | "
2, 294, "Transportation - Audience Seating" | 2, | 294 | , | " | Transportation - Audience Seating | "
2, 295, "Transportation - Terminal—Ticket Counter" | 2, | 295 | , | " | Transportation - Terminal—Ticket Counter | "
2, 296, "Warehouse - Fine Material Storage" | 2, | 296 | , | " | Warehouse - Fine Material Storage | "
2, 297, "Warehouse - Medium/Bulky Material Storage" | 2, | 297 | , | " | Warehouse - Medium/Bulky Material Storage | "