## Fan Static Pressure Adjustments
Key:
Input Values
Intermediate Values
Check Values
PROPOSED
System Name | Type | SupFanCap | RetFanCap | ReliefFanCap | ExhFanCap | SupFanPwr | RetFanPwr | ReliefFanPwr | ExhFanPwr | TotSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | FullDuctExhPDAdj | FullDuctExhLabOrVivPDAdj | ExhFiltersPDAdj | BioCabinetPDAdj | FumeHoodExhPDAdj | LabOrVivExhHiRisePDAdj | SndAttnExhPDAdj |  | FullDuctRetPDAdj | FullDuctRetLabOrVivPDAdj | MERV9To12PDAdj | MERV13To15PDAdj | MERVGTE16PDAdj | GasPhaseAirCleanersPDAdj | ERVPDAdj | EvapHumOrClrPDAdj | SndAttnPDAdj |  | FullDuctExhDevFlow | FullDuctExhLabOrVivDevFlow | ExhFiltersDevFlow | BioCabinetDevFlow | FumeHoodExhDevFlow | LabOrVivExhHiRiseDevFlow | SndAttnExhDevFlow | FullDuctRetDevFlow | FullDuctRetLabOrVivDevFlow | MERV9To12DevFlow | MERV13To15DevFlow | MERVGTE16DevFlow | GasPhaseAirCleanersDevFlow | ERVDevFlow | EvapHumOrClrDevFlow | SndAttnDevFlow | TotSysFanPwrAdj
|  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.)
BottomVAV | PVAV | 17875.9 | 16088.3 |  |  | 14.5711 | 16.6604 |  |  | 31.2315 | 0.46655 | 0.53345 | 0 | 0 | [8 empty] | 0.5 |  |  |  | 1.2 |  |  |  | 0.15 | [8 empty] | 16088 |  |  |  | 17875.9 |  |  |  | 17875.9 | 7.789
Mid VAV-SW Zones | PVAV | 3644.56 | 2962.33 |  |  | 2.7911 | 1.006 |  |  | 3.7971 | 0.73506 | 0.26494 | 0 | 0 | [12 empty] | 1.2 | [16 empty] | 3644.56 |  |  |  |  | 1.0587
Mid VAV NE_Core Zones | PVAV | 14231.4 |  | 13119.8 |  | 11.6756 |  | 3.4449 |  | 15.1205 | 0.77217 | 0 | 0.22783 | 0 | [13 empty] | 1.2 | [16 empty] | 14231.4 |  |  |  | 4.134
Mid SE Zones ExhSys | Exhaust | 0 |  |  | 900 |  |  |  | 0.10307 | 0.10307 | 0 | 0 | 0 | 1 | 0.5 |  |  | 1.1 | [14 empty] | 900 |  |  | 450 | [12 empty] | 0.22876
TopFlrDOAS | SZAC | 1565 |  |  |  | 0.4695 |  |  |  | 0.4695 | 1 | 0 | 0 | 0 | [34 empty] | 0
Top SW Zones ExhSys | Exhaust | 0 |  |  | 400 |  |  |  | 0.045809 | 0.045809 | 0 | 0 | 0 | 1 | [34 empty] | 0
Perim_TopZn1_PTAC | PTAC | 2000 |  |  |  | 0.6 |  |  |  | 0.6 | 1 | 0 | 0 | 0 | [10 empty] | 0.5 | [16 empty] | 2000 | [6 empty] | 0.24207
Perim_TopZn2_PTAC | PTAC | 2000 |  |  |  | 0.6 |  |  |  | 0.6 | 1 | 0 | 0 | 0 | [34 empty] | 0
Perim_TopZn3_PTAC | PTAC | 2000 |  |  |  | 0.6 |  |  |  | 0.6 | 1 | 0 | 0 | 0 | [34 empty] | 0
Perim_TopZn4_PTAC | PTAC | 2000 |  |  |  | 0.6 |  |  |  | 0.6 | 1 | 0 | 0 | 0 | [16 empty] | 0.15 | [16 empty] | 2000 | 0.072622
Core_TopZn_PTAC | PTAC | 3000 |  |  |  | 0.9 |  |  |  | 0.9 | 1 | 0 | 0 | 0 | [34 empty] | 0
13.5252
Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | PriAirCondgSysDsgnFlow | VentSysDsgnFlow | DsgnExhFlow | PriZnToSysAirFlowRatio | VentZnToSysAirFlowRatio | ExhZnToSysAirFlowRatio | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | FullDuctExhFanPwrAdj | FullDuctExhLabOrVivFanPwrAdj | ExhFiltersFanPwrAdj | BioCabinetFanPwrAdj | FumeHoodExhFanPwrAdj | LabOrVivExhHiRiseFanPwrAdj | SndAttnExhFanPwrAdj | TotExhFanPwrAdj | FullDuctRetFanPwrAdj | FullDuctRetLabOrVivFanPwrAdj | MERV9To12FanPwrAdj | MERV13To15FanPwrAdj | MERVGTE16FanPwrAdj | GasPhaseAirCleanersFanPwrAdj | ERVFanPwrAdj | EvapHumOrClrFanPwrAdj | SndAttnFanPwrAdj | TotNonExhFanPwrAdj | TotFanPwrAdj
|  |  |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
Core_bottom Thermal Zone | BottomVAV | BottomVAV |  | 10586.7 | 10586.7 |  | 0.59223 | 0 | 0 | 8.6295 | 9.8668 | 0 | 0 | 18.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1532 | 0 | 0 | 0 | 3.0753 | 0 | 0 | 0 | 0.38441 | 4.6129 | 4.6129
Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV |  | 2231.76 | 2231.76 |  | 0.12485 | 0 | 0 | 1.8192 | 2.08 | 0 | 0 | 3.8992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24311 | 0 | 0 | 0 | 0.6483 | 0 | 0 | 0 | 0.081037 | 0.97244 | 0.97244
Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV |  | 1412.9 | 1412.9 |  | 0.079039 | 0 | 0 | 1.1517 | 1.3168 | 0 | 0 | 2.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15391 | 0 | 0 | 0 | 0.41043 | 0 | 0 | 0 | 0.051304 | 0.61564 | 0.61564
Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV |  | 2231.76 | 2231.76 |  | 0.12485 | 0 | 0 | 1.8192 | 2.08 | 0 | 0 | 3.8992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24311 | 0 | 0 | 0 | 0.6483 | 0 | 0 | 0 | 0.081037 | 0.97244 | 0.97244
Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV |  | 1412.8 | 1412.8 |  | 0.079034 | 0 | 0 | 1.1516 | 1.3167 | 0 | 0 | 2.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1539 | 0 | 0 | 0 | 0.4104 | 0 | 0 | 0 | 0.0513 | 0.6156 | 0.6156
FirstFloor_Plenum Thermal Zone | NONE | NONE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones |  | 10586.7 | 10586.7 |  | 0.7439 | 0 | 0 | 8.6854 | 0 | 2.5626 | 0 | 11.2481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0753 | 0 | 0 | 0 | 3.0753 | 3.0753
Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.76 | 2231.76 | 500 | 0.61235 | 0 | 0.55556 | 1.7091 | 0.61602 | 0 | 0.057261 | 2.3824 | 0.060518 | 0 | 0 | 0.06657 | 0 | 0 | 0 | 0.12709 | 0 | 0 | 0 | 0 | 0.6483 | 0 | 0 | 0 | 0 | 0.6483 | 0.77538
Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | 1412.9 | 1412.9 | 400 | 0.09928 | 0 | 0.44444 | 1.1592 | 0 | 0.34201 | 0.045809 | 1.547 | 0.048414 | 0 | 0 | 0.053256 | 0 | 0 | 0 | 0.10167 | 0 | 0 | 0 | 0 | 0 | 0.41043 | 0 | 0 | 0 | 0.41043 | 0.5121
Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones |  | 2231.76 | 2231.76 |  | 0.15682 | 0 | 0 | 1.831 | 0 | 0.54022 | 0 | 2.3712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6483 | 0 | 0 | 0 | 0.6483 | 0.6483
Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones |  | 1412.8 | 1412.8 |  | 0.38765 | 0 | 0 | 1.082 | 0.38997 | 0 | 0 | 1.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4104 | 0 | 0 | 0 | 0 | 0.4104 | 0.4104
MidFloor_Plenum Thermal Zone | NONE | NONE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS |  | 3000 | 1165 |  | 1 | 0.74441 | 0 | 1.2495 | 0 | 0 | 0 | 1.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Perim_TopZn1_PTAC | Top SW Zones ExhSys | 2000 | 2000 | 245 | 1 | 0 | 0.6125 | 0.6 | 0 | 0 | 0.028058 | 0.62806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24207 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24207 | 0.24207
Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | Perim_TopZn2_PTAC | Top SW Zones ExhSys | 2000 | 2000 | 155 | 1 | 0 | 0.3875 | 0.6 | 0 | 0 | 0.017751 | 0.61775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS |  | 2000 | 245 |  | 1 | 0.15655 | 0 | 0.6735 | 0 | 0 | 0 | 0.6735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS |  | 2000 | 155 |  | 1 | 0.099042 | 0 | 0.6465 | 0 | 0 | 0 | 0.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072622 | 0.072622 | 0.072622
TopFloor_Plenum Thermal Zone | NONE | NONE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.5252
BASELINE
Thermal Zone | PriAirCondgSysRef | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | PriAirCondgSysDsgnFlow | BaseToPropDsgnFlowRat | FullDuctExhFanPwrAdj | FullDuctExhLabOrVivFanPwrAdj | ExhFiltersFanPwrAdj | BioCabinetFanPwrAdj | FumeHoodExhFanPwrAdj | LabOrVivExhHiRiseFanPwrAdj | SndAttnExhFanPwrAdj | TotExhFanPwrAdj | FullDuctRetFanPwrAdj | FullDuctRetLabOrVivFanPwrAdj | MERV9To12FanPwrAdj | MERV13To15FanPwrAdj | MERVGTE16FanPwrAdj | GasPhaseAirCleanersFanPwrAdj | ERVFanPwrAdj | EvapHumOrClrFanPwrAdj | SndAttnFanPwrAdj | TotNonExhFanPwrAdj | TotFanPwrAdj
|  | (kW) | (kW) | (kW) | (kW) | (kW) | (cfm) | (frac) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
Core_bottom Thermal Zone | BaseAirSys6 | 8.6295 | 9.8668 | 0 | 0 | 18.4963 | 5618.35 | 0.5307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61201 | 0 | 0 | 0 | 1.6321 | 0 | 0 | 0 | 0.20401 | 2.4481 | 2.4481
Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys6 | 1.8192 | 2.08 | 0 | 0 | 3.8992 | 1700.44 | 0.76193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18523 | 0 | 0 | 0 | 0.49395 | 0 | 0 | 0 | 0.061744 | 0.74093 | 0.74093
Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys6 | 1.1517 | 1.3168 | 0 | 0 | 2.4685 | 1412.83 | 0.99995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1539 | 0 | 0 | 0 | 0.41041 | 0 | 0 | 0 | 0.051301 | 0.61561 | 0.61561
Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys6 | 1.8192 | 2.08 | 0 | 0 | 3.8992 | 1543.53 | 0.69162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16814 | 0 | 0 | 0 | 0.44837 | 0 | 0 | 0 | 0.056047 | 0.67256 | 0.67256
Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys6 | 1.1516 | 1.3167 | 0 | 0 | 2.4683 | 1572.03 | 1.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17124 | 0 | 0 | 0 | 0.45665 | 0 | 0 | 0 | 0.057082 | 0.68498 | 0.68498
FirstFloor_Plenum Thermal Zone | BaseAirSys6 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_mid Thermal Zone | BaseAirSys6-2 | 8.6854 | 0 | 2.5626 | 0 | 11.2481 | 5741.9 | 0.54237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6679 | 0 | 0 | 0 | 1.6679 | 1.6679
Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys6-2 | 1.7091 | 0.61602 | 0 | 0.057261 | 2.3824 | 1872 | 0.8388 | 0.060518 | 0 | 0 | 0.06657 | 0 | 0 | 0 | 0.12709 | 0 | 0 | 0 | 0 | 0.54379 | 0 | 0 | 0 | 0 | 0.54379 | 0.67088
Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys6-2 | 1.1592 | 0 | 0.34201 | 0.045809 | 1.547 | 1587.29 | 1.1234 | 0.048414 | 0 | 0 | 0.053256 | 0 | 0 | 0 | 0.10167 | 0 | 0 | 0 | 0 | 0 | 0.46109 | 0 | 0 | 0 | 0.46109 | 0.56276
Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys6-2 | 1.831 | 0 | 0.54022 | 0 | 2.3712 | 1666.53 | 0.74673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4841 | 0 | 0 | 0 | 0.4841 | 0.4841
Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys6-2 | 1.082 | 0.38997 | 0 | 0 | 1.4719 | 1789.05 | 1.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51969 | 0 | 0 | 0 | 0 | 0.51969 | 0.51969
MidFloor_Plenum Thermal Zone | BaseAirSys6-2 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_top Thermal Zone | BaseAirSys6-3 | 1.2495 | 0 | 0 | 0 | 1.2495 | 5847.76 | 1.9493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_1 Thermal Zone | BaseAirSys6-3 | 0.6 | 0 | 0 | 0.028058 | 0.62806 | 1921.59 | 0.96079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23258 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23258 | 0.23258
Perimeter_top_ZN_2 Thermal Zone | BaseAirSys6-3 | 0.6 | 0 | 0 | 0.017751 | 0.61775 | 1591.52 | 0.79576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_3 Thermal Zone | BaseAirSys6-3 | 0.6735 | 0 | 0 | 0 | 0.6735 | 1738.78 | 0.86939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_4 Thermal Zone | BaseAirSys6-3 | 0.6465 | 0 | 0 | 0 | 0.6465 | 1845.72 | 0.92286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06702 | 0.06702 | 0.06702
TopFloor_Plenum Thermal Zone | BaseAirSys6-3 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.3671
System Name | Type | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | TotPropSysFanPwr | TotExhSysFanPwrAdj | TotNonExhSysFanPwrAdj | TotSysFanPwrAdj
|  | (frac.) | (frac.) | (frac.) | (frac.) | (kW) | (BHP) | (BHP) | (BHP)
BaseAirSys6 |  | 0.46655 | 0.53345 | 0 | 0 | 31.2315 | 0 | 5.1621 | 5.1621
BaseAirSys6-2 |  | 0.76058 | 0.05289 | 0.18111 | 0.0054189 | 19.0206 | 0.22876 | 3.6766 | 3.9054
BaseAirSys6-3 |  | 0.98799 | 0 | 0 | 0.012007 | 3.8153 | 0 | 0.2996 | 0.2996
9.3671

## Fan Power Ratios - SP
Key:
Input Values
Intermediate Values
Check Values
PROPOSED
[7 empty] | 1 | [8 empty] | 3.363
|  |  |  | Flows |  |  | Ratios |  |  | Zone Fan Pwrs
Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | PriAirCondgSysDsgnFlow | VentSysDsgnFlow | DsgnExhFlow | PriZnToSysFlowRat | VentZnToSysFlowRat | ExhZnToSysAirFlowRatio | PriSysPropSupFanPwr | VentSysPropSupFanPwr | TotPropSupFanPwr | PriSysPropRetFanPwr | VentSysPropRetFanPwr | TotPropRetFanPwr | PriSysPropReliefFanPwr | VentSysPropReliefFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPriSysPropFanPwr | TotVentSysPropFanPwr | TotPropFanPwr
|  |  |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW)
Core_bottom Thermal Zone | Bottom VAV | Bottom VAV |  | 10586.7 | 10586.7 | 0 | 0.59223 | - | - | 8.6294 | - | 8.6294 | 9.8668 | - | 9.8668 | 0 | - | 0 | - | 18.4962 | - | 18.4962
Perimeter_bot_ZN_1 Thermal Zone | Bottom VAV | Bottom VAV |  | 2231.76 | 2231.76 | 0 | 0.12485 | - | - | 1.8192 | - | 1.8192 | 2.08 | - | 2.08 | 0 | - | 0 | - | 3.8992 | - | 3.8992
Perimeter_bot_ZN_2 Thermal Zone | Bottom VAV | Bottom VAV |  | 1412.9 | 1412.9 | 0 | 0.079039 | - | - | 1.1517 | - | 1.1517 | 1.3168 | - | 1.3168 | 0 | - | 0 | - | 2.4685 | - | 2.4685
Perimeter_bot_ZN_3 Thermal Zone | Bottom VAV | Bottom VAV |  | 2231.76 | 2231.76 | 0 | 0.12485 | - | - | 1.8192 | - | 1.8192 | 2.08 | - | 2.08 | 0 | - | 0 | - | 3.8992 | - | 3.8992
Perimeter_bot_ZN_4 Thermal Zone | Bottom VAV | Bottom VAV |  | 1412.8 | 1412.8 | 0 | 0.079033 | - | - | 1.1516 | - | 1.1516 | 1.3167 | - | 1.3167 | 0 | - | 0 | - | 2.4683 | - | 2.4683
Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NW_Core Zones |  | 10586.7 | 10586.7 | 0 | 0.7439 | - | - | 8.6854 | - | 8.6854 | 0 | - | 0 | 2.5017 | - | 2.5017 | - | 11.1872 | - | 11.1872
Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.76 | 2231.76 | 500 | 0.61235 | - | 0.55556 | 1.7091 | - | 1.7091 | 0.68211 | - | 0.68211 | 0 | - | 0 | 0.057261 | 2.3913 | - | 2.4485
Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NW_Core Zones | Mid SE Zones ExhSys | 1412.9 | 1412.9 | 400 | 0.09928 | - | 0.44444 | 1.1592 | - | 1.1592 | 0 | - | 0 | 0.33388 | - | 0.33388 | 0.045809 | 1.493 | - | 1.5388
Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NW_Core Zones |  | 2231.76 | 2231.76 | 0 | 0.15682 | - | - | 1.831 | - | 1.831 | 0 | - | 0 | 0.52738 | - | 0.52738 | - | 2.3583 | - | 2.3583
Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones |  | 1412.8 | 1412.8 | 0 | 0.38765 | - | - | 1.082 | - | 1.082 | 0.4318 | - | 0.4318 | 0 | - | 0 | - | 1.5138 | - | 1.5138
Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS |  | 3000 | 1165 | 0 | 1 | 0.74441 | - | 0.9 | 0.3495 | 1.2495 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0.9 | 0.3495 | 1.2495
Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC |  | Top SW Zones ExhSys | 2000 | 2000 | 245 | 1 | - | 0.6125 | 0.6 | - | 0.6 | 0 | - | 0 | 0 | - | 0 | 0.028058 | 0.6 | - | 0.62806
Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC |  | Top SW Zones ExhSys | 2000 | 2000 | 155 | 1 | - | 0.3875 | 0.6 | - | 0.6 | 0 | - | 0 | 0 | - | 0 | 0.017751 | 0.6 | - | 0.61775
Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS |  | 2000 | 245 | 0 | 1 | 0.15655 | - | 0.6 | 0.0735 | 0.6735 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0.6 | 0.0735 | 0.6735
Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS |  | 2000 | 155 | 0 | 1 | 0.099042 | - | 0.6 | 0.0465 | 0.6465 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0.6 | 0.0465 | 0.6465
Systems |  |  |  | SupFanCap | SupFanPwr | RetFanCap | RetFanPwr | ReliefFanCap | ReliefFanPwr | ExhFlow | ExhFanPwr | TotPropSysFanPwr | TotPropSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio
|  |  |  | (cfm) | (kW) | (cfm) | (kW) | (cfm) | (kW) | (cfm) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.)
Bottom VAV |  |  |  | 17876 | 14.5711 | 16088.3 | 16.6604 |  |  |  | 0 | 31.2315 | 31.2314 | 0.46655 | 0.53345 | 0 | 0
Mid VAV-SW Zones |  |  |  | 3644.56 | 2.7911 | 3280.11 | 1.1139 |  |  |  | 0 | 3.905 | 3.905 | 0.71475 | 0.28525 | 0 | 0
Mid VAV NE_Core Zones |  |  |  | 14231.4 | 11.6756 |  |  | 13830.5 | 3.363 |  | 0 | 15.0386 | 15.0386 | 0.77638 | 0 | 0.22362 | 0
Mid SE Zones ExhSys |  |  |  | 0 | 0 |  |  |  |  | 900 | 0.10307 | 0.10307 | 0.10307 | 0 | 0 | 0 | 1
Core_TopZn_PTAC |  |  |  | 3000 | 0.9 | [5 empty] | 0 | 0.9 | 0.9 | 1 | 0 | 0 | 0
Perim_TopZn1_PTAC |  |  |  | 2000 | 0.6 | [5 empty] | 0 | 0.6 | 0.6 | 1 | 0 | 0 | 0
Perim_TopZn2_PTAC |  |  |  | 2000 | 0.6 | [5 empty] | 0 | 0.6 | 0.6 | 1 | 0 | 0 | 0
Perim_TopZn3_PTAC |  |  |  | 2000 | 0.6 | [5 empty] | 0 | 0.6 | 0.6 | 1 | 0 | 0 | 0
Perim_TopZn4_PTAC |  |  |  | 2000 | 0.6 | [5 empty] | 0 | 0.6 | 0.6 | 1 | 0 | 0 | 0
TopFlrDOAS |  |  |  | 1565 | 0.4695 | [5 empty] | 0 | 0.4695 | 0.4695 | 1 | 0 | 0 | 0
Top SW Zones ExhSys |  |  |  | 0 | 0 |  |  |  |  | 400 | 0.045809 | 0.045809 | 0.045809 | 0 | 0 | 0 | 1
BASELINE
Zone Fan Powers
Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | ZnToSysExhFanPwrRatio | ExhFanMtrBHP
|  |  |  | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (bhp)
Core_bottom Thermal Zone | BaseAirSys6 |  |  | 8.6294 | 9.8668 | 0 | - | 18.4962 | - | -
Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys6 |  |  | 1.8192 | 2.08 | 0 | - | 3.8992 | - | -
Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys6 |  |  | 1.1517 | 1.3168 | 0 | - | 2.4685 | - | -
Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys6 |  |  | 1.8192 | 2.08 | 0 | - | 3.8992 | - | -
Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys6 |  |  | 1.1516 | 1.3167 | 0 | - | 2.4683 | - | -
Core_mid Thermal Zone | BaseAirSys6-2 |  |  | 8.6854 | 0 | 2.5017 | - | 11.1872 | - | -
Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys6-2 |  |  | 1.7091 | 0.68211 | 0 | 0.057261 | 2.4485 | 0.55556 | 0.061207
Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys6-2 |  |  | 1.1592 | 0 | 0.33388 | 0.045809 | 1.5388 | 0.44444 | 0.048966
Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys6-2 |  |  | 1.831 | 0 | 0.52738 | - | 2.3583 | - | -
Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys6-2 |  |  | 1.082 | 0.4318 | 0 | - | 1.5138 | - | -
Core_top Thermal Zone | BaseAirSys6-3 |  |  | 1.2495 | 0 | 0 | - | 1.2495 | - | -
Perimeter_top_ZN_1 Thermal Zone | BaseAirSys6-3 |  |  | 0.6 | 0 | 0 | 0.028058 | 0.62806 | 0.6125 | 0.12596
Perimeter_top_ZN_2 Thermal Zone | BaseAirSys6-3 |  |  | 0.6 | 0 | 0 | 0.017751 | 0.61775 | 0.3875 | 0.079692
Perimeter_top_ZN_3 Thermal Zone | BaseAirSys6-3 |  |  | 0.6735 | 0 | 0 | - | 0.6735 | - | -
Perimeter_top_ZN_4 Thermal Zone | BaseAirSys6-3 |  |  | 0.6465 | 0 | 0 | - | 0.6465 | - | -
MtrBHP
Systems |  |  |  | SupFanCap | TotPropSysFanPwr | PropExhFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | BaseFanBHPAllowance | BaseFanBHPWithPressDropCredit | Supply Fan | Return Fan | Relief Fan | Ret+Rel Fan | Exhaust Fan
|  |  |  | (cfm) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
BaseAirSys6 |  |  |  | 11847.2 | 31.2314 | 0 | 0.46655 | 0.53345 | 0 | 0 | 15.4014 | 20.5635 | 9.5939 | 10.9696 | 0 | 10.9696 | 0
BaseAirSys6-2 |  |  |  | 12656.8 | 19.0466 | 0.10307 | 0.75954 | 0.058483 | 0.17657 | 0.0054115 | 16.4538 | 20.3592 | 15.4636 | 1.1907 | 3.5947 | 4.7854 | 0.11017
BaseAirSys6-3 |  |  |  | 12945.4 | 3.8153 | 0.045809 | 0.98799 | 0 | 0 | 0.012007 | 16.829 | 17.1286 | 16.923 | 0 | 0 | 0 | 0.20566