## Sheet1
;
TABLE T24N_2022FanPwrIdxAdj
; |  |  | Exhaust systems required by code to be fully ducted | Return systems required by code to be fully ducted | Exhaust filters, scrubbers, or other exhaust treatment (calculation required, see note) | Particulate filtration credit: MERV 16 or greater and electronically enhanced filters | Carbon and other gas-phase air cleaners (calculation required, see note) | Biosafety cabinet (calculation required, see note) | Exhaust Systems Base Allowance | Supply - Energy Recovery (Enthalpy Recovery Ratio ? 0.60 and <0.65) | Return - Energy Recovery (Enthalpy Recovery Ratio ? 0.60 and <0.65) | Return - Filter (any MERV value) | Single Zone VAV Systems that are capable of turning down to 50% of full load airflow at a maximum of 30% design wattage
| SysType | FlowCap | FullyDuctedExh | FullyDuctedRet | ExhFilters | MERVGTE16 | GasPhaseAirCleaners | BiosftyCabExh | ExhBaseAllow | ERVSupply | ERVReturn | RetFilter | SZVAV
| MultiZoneVAV | <=5000 | 0.089 | 0.089 | 0.177 | 0.265 | 0.176 | 0.177 | 0.221 | 0.184 | 0.19 | 0.046 | 0
| MultiZoneVAV | <=10000 | 0.1 | 0.1 | 0.198 | 0.28 | 0.188 | 0.198 | 0.246 | 0.155 | 0.163 | 0.041 | 0
| MultiZoneVAV | >10000 | 0.116 | 0.116 | 0.231 | 0.333 | 0.224 | 0.231 | 0.236 | 0.144 | 0.146 | 0.036 | 0
| AllOther | <=5000 | 0.091 | 0.091 | 0.179 | 0.264 | 0.177 | 0.179 | 0.186 | 0.19 | 0.191 | 0.046 | 0.07
| AllOther | <=10000 | 0.102 | 0.102 | 0.202 | 0.292 | 0.197 | 0.202 | 0.184 | 0.163 | 0.166 | 0.041 | 0.1
| AllOther | >10000 | 0.116 | 0.116 | 0.232 | 0.342 | 0.231 | 0.232 | 0.19 | 0.146 | 0.148 | 0.036 | 0.089
ENDTABLE
;
TABLE T24N_2022BaseFanPwrIdx
; |  |  | 3a – SZAC | 3b – SZHP (no furnace) | 3c – SZDFHP (with furnace) | 7a – SZVAVAC | 7b – SZVAVHP | 7c – SZVAVDFHP (with furnace) | 5 – PVAV | 6 – VAV | 9 – HEATVENT
|  | FlowCap | Sys3a | Sys3b | Sys3c | Sys7a | Sys7b | Sys7c | Sys5 | Sys6 | Sys9
|  | <=5000 | 0.802 | 0.744 | 0.802 | 0.802 | 0.744 | 0.802 | 1 | 0.977 | 0.616
|  | <=10000 | 0.78 | 0.72 | 0.78 | 0.78 | 0.72 | 0.78 | 1.022 | 1.013 | 0.62
|  | >10000 | 0.748 | 0.676 | 0.748 | 0.748 | 0.676 | 0.748 | 0.964 | 0.947 | 0.605
ENDTABLE