## Results
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  |  |  | 9 |  | 10 |  | 10 |  | 11 | [5 empty] | 12 |  | 13 |  |  |  | 14 |  | 16
| Version number | Test Case | Annual TDV EUI (excludes Receptacle, Process, Process Ltg) |  | Site Energy EUI - Electricity (excludes Receptacle, Process, Process Ltg) |  | Site Energy EUI - Natural Gas (excludes Receptacle, Process, Process Ltg) |  | Annual Total End Use Site Energy EUI (excludes Receptacle, Process, Process Ltg) |  | Annual End Use Site Energy EUI | [17 empty] | Unmet Load Hours (UMLH) (Heating + Cooling) |  |  |  | Variation from Baseline | [5 empty] | Pass/Fail
| CBECC-Com 2016.2.1 |  | (kBtu/sqft) |  | (kwh/sqft) |  | (therm/sqft) |  | (kBtu/sqft) |  | Heating (kBtu/sqft) |  | Cooling (kBtu/sqft) |  | Interior Lighting (kBtu/sqft) |  | Gas Equipment (kBtu/sqft) |  | Electric Equipment (kBtu/sqft) |  | Fans (kBtu/sqft) |  | Pumps (kBtu/sqft) |  | Tower (kBtu/sqft) |  | Water Heating (kBtu/sqft) |  | Number of Zones with Total UMLH > 150 |  | Zone Max Total UMLH (Hr/yr) |  | TDV % variation |  | Total End Use Site Energy % Variation |  |  |  |  | Floor Area
|  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model
| CBECC-Com 2016.2.1 | 0500015-RetlMed-Baseline | 265.481 |  | 9.2948 |  | 0.04154 |  | 35.8683 |  | 0.33305 |  | 13.4546 |  | 8.1228 |  | 0 |  | 10.7303 |  | 10.1378 |  | 0 |  | 0 |  | 3.82 |  | 0 |  | 0 | [8 empty] | 24695
| CBECC-Com 2016.2.1 | 0500115-RetlMed-EnvelopeRoofInsulation | 263.295 |  | 9.2253 |  | 0.041223 |  | 35.5993 |  | 0.30129 |  | 13.2176 |  | 8.1228 |  | 0 |  | 10.7303 |  | 10.1376 |  | 0 |  | 0 |  | 3.82 |  | 0 |  | 0 |  | -0.8234% |  | -0.7476% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0500215-RetlMed-EnvelopeWallInsulation | 263.247 |  | 9.2344 |  | 0.040935 |  | 35.6017 |  | 0.27249 |  | 13.2488 |  | 8.1228 |  | 0 |  | 10.7303 |  | 10.1376 |  | 0 |  | 0 |  | 3.82 |  | 0 |  | 0 |  | -0.8415% |  | -0.6496% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0500315-RetlMed-EnvelopeHeavy | 263.998 |  | 9.2501 |  | 0.040934 |  | 35.6551 |  | 0.27241 |  | 13.3023 |  | 8.1228 |  | 0 |  | 10.7303 |  | 10.1376 |  | 0 |  | 0 |  | 3.82 |  | 0 |  | 0 |  | -0.5586% |  | -0.4805% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0512815-RetlMed-SZVAV | 235.952 |  | 7.843 |  | 0.043471 |  | 31.1074 |  | 0.52602 |  | 13.5844 |  | 8.1228 |  | 0 |  | 10.7303 |  | 5.0541 |  | 0 |  | 0 |  | 3.82 |  | 0 |  | 0 |  | -11.12% |  | -15.62% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0500006-RetlMed-Baseline | 176.892 |  | 6.1662 |  | 0.049608 |  | 25.9996 |  | 0.54968 |  | 3.5173 |  | 7.7718 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.4099 |  | 0 |  | 0 | [8 empty] | 24695
| CBECC-Com 2016.2.1 | 0500706-RetlMed-EnvelopeRoofInsulation | 175.836 |  | 6.1379 |  | 0.049129 |  | 25.8552 |  | 0.5018 |  | 3.4207 |  | 7.7718 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.4099 |  | 0 |  | 0 |  | -0.597% |  | -0.459% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0500806-RetlMed-EnvelopeWallInsulation | 176.331 |  | 6.1595 |  | 0.048585 |  | 25.8744 |  | 0.44743 |  | 3.4943 |  | 7.7718 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.4099 |  | 0 |  | 0 |  | -0.3171% |  | -0.109% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0500906-RetlMed-EnvelopeHeavy | 174.581 |  | 6.1099 |  | 0.048498 |  | 25.6964 |  | 0.43877 |  | 3.325 |  | 7.7718 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.4098 |  | 0 |  | 0 |  | -1.306% |  | -0.9141% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0513006-RetlMed-SZVAV | 129.62 |  | 4.114 |  | 0.055488 |  | 19.5849 |  | 1.1376 |  | 4.3665 |  | 7.7718 |  | 0 |  | 10.7303 |  | 1.8991 |  | 0 |  | 0 |  | 4.4099 |  | 0 |  | 0 |  | -26.72% |  | -33.28% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0300016-OffMed-Baseline | 109.061 |  | 2.8701 |  | 0.12607 |  | 22.3968 |  | 11.2828 |  | 2.847 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.6801 |  | 0.27076 |  | 0 |  | 1.3233 |  | 0 |  | 0 | [8 empty] | 53600
| CBECC-Com 2016.2.1 | 0301516-OffMed-FloorSlabInsulation | 108.899 |  | 2.8767 |  | 0.12335 |  | 22.1477 |  | 11.011 |  | 2.8628 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.6903 |  | 0.2674 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -0.1485% |  | 0.2308% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0303216-OffMed-LightingLowLPD | 101.417 |  | 2.5519 |  | 0.13045 |  | 21.7498 |  | 11.7216 |  | 2.7894 |  | 3.9942 |  | 0 |  | 14.6226 |  | 1.6422 |  | 0.27902 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -7.009% |  | -11.09% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0303316-OffMed-LightingHighLPD | 116.764 |  | 3.1898 |  | 0.12179 |  | 23.0605 |  | 10.8555 |  | 2.9055 |  | 5.9914 |  | 0 |  | 14.6226 |  | 1.7213 |  | 0.26359 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | 7.063% |  | 11.14% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0301716-OffMed-GlazingWindowU | 107.858 |  | 2.8783 |  | 0.11671 |  | 21.4893 |  | 10.3471 |  | 2.8698 |  | 4.993 |  | 0 |  | 14.6226 |  | 1.6964 |  | 0.25965 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -1.103% |  | 0.2854% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0301816-OffMed-GlazingWindowSHGC | 107.742 |  | 2.8176 |  | 0.13227 |  | 22.8376 |  | 11.9027 |  | 2.7192 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.6165 |  | 0.28304 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -1.209% |  | -1.827% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0301916-OffMed-GlazingWindowUSHGC | 106.444 |  | 2.8235 |  | 0.12261 |  | 21.8918 |  | 10.9368 |  | 2.7395 |  | 4.993 |  | 0 |  | 14.6226 |  | 1.6282 |  | 0.27101 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -2.4% |  | -1.624% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0307216-OffMed-HVACPVAV Design | 105.187 |  | 2.7198 |  | 0.12772 |  | 22.0494 |  | 11.4481 |  | 2.7915 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.2216 |  | 0.27205 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -3.552% |  | -5.235% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0307316-OffMed-HVACPVAV SATControl | 117.889 |  | 3.1966 |  | 0.15648 |  | 26.5519 |  | 14.3245 |  | 4.1202 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.4648 |  | 0.32618 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | 8.095% |  | 11.38% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0307516-OffMed-HVACPVAV EconomizerType | 109.235 |  | 2.8804 |  | 0.12607 |  | 22.4319 |  | 11.2827 |  | 2.8819 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.6804 |  | 0.27075 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | 0.1595% |  | 0.3595% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0314116-OffMed-FanPwrBox | 138.01 |  | 4.3407 |  | 0.10132 |  | 24.941 |  | 8.8086 |  | 3.0705 |  | 4.9928 |  | 0 |  | 14.6226 |  | 6.5735 |  | 0.17227 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | 26.54% |  | 51.24% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0312616-OffMed-Plenum | 107.564 |  | 2.8458 |  | 0.12427 |  | 22.1344 |  | 11.1032 |  | 2.8006 |  | 4.9928 |  | 0 |  | 14.6226 |  | 1.6329 |  | 0.28156 |  | 0 |  | 1.3233 |  | 0 |  | 0 |  | -1.373% |  | -0.8457% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0300006-OffMed-Baseline | 107.797 |  | 3.4203 |  | 0.035285 |  | 15.1983 |  | 2.3922 |  | 5.1257 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.4415 |  | 0.1094 |  | 0 |  | 1.136 |  | 0 |  | 0 | [8 empty] | 53600
| CBECC-Com 2016.2.1 | 0302006-OffMed-FloorSlabInsulation | 108.028 |  | 3.4293 |  | 0.034574 |  | 15.1576 |  | 2.3211 |  | 5.1515 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.4488 |  | 0.1068 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | 0.2143% |  | 0.2613% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0302206-OffMed-GlazingWindowU | 107.779 |  | 3.4384 |  | 0.032393 |  | 14.9709 |  | 2.1029 |  | 5.1754 |  | 4.9937 |  | 0 |  | 14.6226 |  | 1.4603 |  | 0.1026 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -0.0167% |  | 0.5296% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0302306-OffMed-GlazingWindowSHGC | 105.461 |  | 3.341 |  | 0.03798 |  | 15.1971 |  | 2.6616 |  | 4.911 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.3772 |  | 0.11776 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -2.167% |  | -2.318% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0302406-OffMed-GlazingWindowUSHGC | 105.344 |  | 3.3566 |  | 0.034849 |  | 14.9371 |  | 2.3485 |  | 4.9553 |  | 4.9937 |  | 0 |  | 14.6226 |  | 1.393 |  | 0.11069 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -2.276% |  | -1.864% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0303406-OffMed-LightingLowLPD | 99.243 |  | 3.0805 |  | 0.037192 |  | 14.2294 |  | 2.5829 |  | 5.0004 |  | 3.9948 |  | 0 |  | 14.6226 |  | 1.3999 |  | 0.11535 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -7.935% |  | -9.936% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0303506-OffMed-LightingHighLPD | 116.414 |  | 3.7616 |  | 0.033552 |  | 16.1895 |  | 2.2189 |  | 5.252 |  | 5.9922 |  | 0 |  | 14.6226 |  | 1.4864 |  | 0.10404 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | 7.994% |  | 9.978% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0307606-OffMed-HVACPVAV Design | 104.077 |  | 3.2752 |  | 0.035688 |  | 14.7433 |  | 2.4325 |  | 5.0235 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.048 |  | 0.10985 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -3.451% |  | -4.243% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0307706-OffMed-HVACPVAV SATControl | 131.93 |  | 4.377 |  | 0.085256 |  | 23.4585 |  | 7.3891 |  | 8.6379 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.1148 |  | 0.18708 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | 22.39% |  | 27.97% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0307906-OffMed-HVACPVAV EconomizerType | 106.905 |  | 3.3996 |  | 0.035285 |  | 15.1276 |  | 2.3921 |  | 5.0542 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.4423 |  | 0.10937 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -0.8275% |  | -0.6055% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0314206-OffMed-FanPwrBox | 131.253 |  | 4.5223 |  | 0.026341 |  | 18.0641 |  | 1.4978 |  | 5.461 |  | 4.9935 |  | 0 |  | 14.6226 |  | 4.9167 |  | 0.059187 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | 21.76% |  | 32.22% |  | Yes | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0312706-OffMed-Plenum | 106.843 |  | 3.3787 |  | 0.036992 |  | 15.227 |  | 2.5629 |  | 5.0293 |  | 4.9935 |  | 0 |  | 14.6226 |  | 1.3853 |  | 0.11999 |  | 0 |  | 1.136 |  | 0 |  | 0 |  | -0.885% |  | -1.216% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0314716-OffMed-LabwExhPVAV | 322.926 |  | 7.1943 |  | 0.85248 |  | 109.7752 |  | 83.9082 |  | 5.7834 |  | 7.35 |  | 5.3869 |  | 16.4716 |  | 10.2318 |  | 1.1643 |  | 0 |  | 1.3376 |  | 0 |  | 0 | [8 empty] | 53600
| CBECC-Com 2016.2.1 | 0313516-OffMed-LabwExhDOAS | 313.434 |  | 7.1346 |  | 0.81558 |  | 105.8825 |  | 80.2185 |  | 3.1546 |  | 7.35 |  | 5.3869 |  | 16.4716 |  | 13.2094 |  | 0.61232 |  | 0 |  | 1.3376 |  | 0 |  | 0 |  | -2.939% |  | -0.8309% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0314806-OffMed-LabwExhPVAV | 314.517 |  | 9.0021 |  | 0.53211 |  | 83.9153 |  | 52.0621 |  | 12.2059 |  | 7.3507 |  | 5.3869 |  | 16.4716 |  | 10.0625 |  | 1.086 |  | 0 |  | 1.1482 |  | 0 |  | 0 | [8 empty] | 53600
| CBECC-Com 2016.2.1 | 0313606-OffMed-LabwExhDOAS | 261.106 |  | 7.5825 |  | 0.38282 |  | 64.1455 |  | 37.1329 |  | 5.2919 |  | 7.3507 |  | 5.3869 |  | 16.4716 |  | 12.7184 |  | 0.50344 |  | 0 |  | 1.1482 |  | 0 |  | 0 |  | -16.98% |  | -15.77% |  | No | Yes | Fail | 53600
| CBECC-Com 2016.2.1 | 0400016-OffLrg-Baserun | 90.3622 |  | 2.6274 |  | 0.10909 |  | 19.8962 |  | 9.6048 |  | 1.149 |  | 5.0106 |  | 0 |  | 14.645 |  | 1.8732 |  | 0.9289 |  | 0.025804 |  | 1.3039 |  | 0 |  | 0 | [8 empty] | 498600
| CBECC-Com 2016.2.1 | 0408416-OffLrg-HVACChillerCOP | 87.0093 |  | 2.5672 |  | 0.10909 |  | 19.6347 |  | 9.6048 |  | 0.91142 |  | 5.0106 |  | 0 |  | 14.645 |  | 1.8732 |  | 0.90544 |  | 0.025316 |  | 1.3039 |  | 0 |  | 0 |  | -3.711% |  | -2.29% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0408516-OffLrg-HVACChWdeltaT | 88.977 |  | 2.6073 |  | 0.10909 |  | 19.822 |  | 9.6048 |  | 1.0738 |  | 5.0106 |  | 0 |  | 14.645 |  | 1.8738 |  | 0.93013 |  | 0.024941 |  | 1.3039 |  | 0 |  | 0 |  | -1.533% |  | -0.7634% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0400006-OffLrg-Baserun | 92.5642 |  | 3.1288 |  | 0.044012 |  | 15.0799 |  | 3.2842 |  | 2.4002 |  | 4.9857 |  | 0 |  | 14.645 |  | 1.7086 |  | 1.5697 |  | 0.014755 |  | 1.1167 |  | 0 |  | 0 | [8 empty] | 498600
| CBECC-Com 2016.2.1 | 0408806-OffLrg-HVACChillerCOP | 86.867 |  | 2.9683 |  | 0.044012 |  | 14.5399 |  | 3.2842 |  | 1.9039 |  | 4.9857 |  | 0 |  | 14.645 |  | 1.7086 |  | 1.5262 |  | 0.014463 |  | 1.1167 |  | 0 |  | 0 |  | -6.155% |  | -5.128% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0408906-OffLrg-HVACChWdeltaT | 88.4736 |  | 3.0285 |  | 0.044016 |  | 14.764 |  | 3.2846 |  | 2.0826 |  | 4.9857 |  | 0 |  | 14.645 |  | 1.7078 |  | 1.5739 |  | 0.012746 |  | 1.1167 |  | 0 |  | 0 |  | -4.419% |  | -3.205% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 1000015-RetlStrp-BaselinePSZ | 317.838 |  | 11.249 |  | 0.052439 |  | 43.6257 |  | 0.28033 |  | 15.541 |  | 10.0978 |  | 0 |  | 12.4077 |  | 12.7443 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 | [8 empty] | 22500
| CBECC-Com 2016.2.1 | 1009215-RetlStrp-HVACPSZ DXCOP | 293.49 |  | 10.5138 |  | 0.052439 |  | 41.1171 |  | 0.28033 |  | 13.0325 |  | 10.0978 |  | 0 |  | 12.4077 |  | 12.7443 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 |  | -7.661% |  | -6.536% |  | No | Yes | Fail | 22500
4 | CBECC-Com 2016.2.1 | 1009315-RetlStrp-HVACPSZ HeatEff | 317.797 |  | 11.249 |  | 0.052189 |  | 43.6008 |  | 0.25541 |  | 15.541 |  | 10.0978 |  | 0 |  | 12.4077 |  | 12.7443 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 |  | -0.0129% |  | 0% |  | No | Yes | Fail | 22500
18 | CBECC-Com 2016.2.1 | 1009415-RetlStrp-HVACPSZ EconomizerControl | 327.152 |  | 11.7999 |  | 0.052173 |  | 45.479 |  | 0.25382 |  | 17.4209 |  | 10.0978 |  | 0 |  | 12.4077 |  | 12.7443 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 |  | 2.93% |  | 4.898% |  | Yes | Yes | Fail | 22500
19 | CBECC-Com 2016.2.1 | 1013715-RetlStrp-EvapCooler | 279.196 |  | 9.5792 |  | 0.052365 |  | 37.9209 |  | 0.27297 |  | 9.8436 |  | 10.0978 |  | 0 |  | 12.4077 |  | 12.7443 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 |  | -12.16% |  | -14.84% |  | No | Yes | Fail | 22500
5 | CBECC-Com 2016.2.1 | 1000006-RetlStrp-BaselinePSZ | 201.146 |  | 7.0112 |  | 0.0625 |  | 30.1716 |  | 0.52467 |  | 4.1621 |  | 9.9577 |  | 0 |  | 12.4077 |  | 9.8033 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 | [8 empty] | 22500
20 | CBECC-Com 2016.2.1 | 1009806-RetlStrp-HVACPSZ DXCOP | 185.787 |  | 6.6182 |  | 0.0625 |  | 28.8308 |  | 0.52467 |  | 2.8214 |  | 9.9577 |  | 0 |  | 12.4077 |  | 9.8033 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 |  | -7.636% |  | -5.605% |  | No | Yes | Fail | 22500
21 | CBECC-Com 2016.2.1 | 1009906-RetlStrp-HVACPSZ HeatEff | 201.068 |  | 7.0112 |  | 0.062033 |  | 30.125 |  | 0.47804 |  | 4.1621 |  | 9.9577 |  | 0 |  | 12.4077 |  | 9.8033 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 |  | -0.03878% |  | 0% |  | No | Yes | Fail | 22500
3 | CBECC-Com 2016.2.1 | 1010006-RetlStrp-HVACPSZ EconomizerControl | 220.549 |  | 8.0936 |  | 0.0618 |  | 33.7948 |  | 0.45466 |  | 7.8553 |  | 9.9577 |  | 0 |  | 12.4077 |  | 9.8033 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 |  | 9.646% |  | 15.44% |  | Yes | Yes | Fail | 22500
22 | CBECC-Com 2016.2.1 | 1013906-RetlStrp-EvapCooler | 177.938 |  | 6.323 |  | 0.0625 |  | 27.8234 |  | 0.52469 |  | 1.8139 |  | 9.9577 |  | 0 |  | 12.4077 |  | 9.8033 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 |  | -11.54% |  | -9.816% |  | No | Yes | Fail | 22500
23 | CBECC-Com 2016.2.1 | 1000015-RetlStrp-BaselinePTAC | 276.02 |  | 9.4952 |  | 0.049635 |  | 37.361 |  | 0.28164 |  | 14.7423 |  | 10.0978 |  | 0 |  | 12.4077 |  | 7.277 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 | [8 empty] | 22500
4 | CBECC-Com 2016.2.1 | 1010115-RetlStrp-HVACPTAC DXCOP | 252.568 |  | 8.7977 |  | 0.049635 |  | 34.9815 |  | 0.28164 |  | 12.3628 |  | 10.0978 |  | 0 |  | 12.4077 |  | 7.277 |  | 0 |  | 0 |  | 4.9623 |  | 0 |  | 0 |  | -8.496% |  | -7.345% |  | No | Yes | Fail | 22500
24 | CBECC-Com 2016.2.1 | 1014315-RetlStrp-WSHP | 264.6 |  | 9.0085 |  | 0.05386 |  | 36.1229 |  | 0.44665 |  | 14.2061 |  | 10.0978 |  | 0 |  | 12.4077 |  | 5.6124 |  | 0.79776 |  | 6.3706e-05 |  | 4.9623 |  | 0 |  | 0 |  | -4.137% |  | -5.125% |  | No | Yes | Fail | 22500
33 | CBECC-Com 2016.2.1 | 1010515-RetlStrp-FPFC | 251.371 |  | 9.6308 |  | 0.053337 |  | 38.1939 |  | 0.37025 |  | 10.1821 |  | 10.0978 |  | 0 |  | 12.4077 |  | 9.1355 |  | 3.3239 |  | 0.12217 |  | 4.9623 |  | 0 |  | 0 |  | -8.93% |  | 1.428% |  | No | Yes | Fail | 22500
30 | CBECC-Com 2016.2.1 | 1000006-RetlStrp-BaselinePTAC | 173.575 |  | 5.897 |  | 0.057252 |  | 25.8452 |  | 0.4929 |  | 4.0583 |  | 9.9577 |  | 0 |  | 12.4077 |  | 5.6125 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 | [8 empty] | 22500
27 | CBECC-Com 2016.2.1 | 1010306-RetlStrp-HVACPTAC DXCOP | 164.958 |  | 5.705 |  | 0.057252 |  | 25.1901 |  | 0.4929 |  | 3.4032 |  | 9.9577 |  | 0 |  | 12.4077 |  | 5.6125 |  | 0 |  | 0 |  | 5.7238 |  | 0 |  | 0 |  | -4.964% |  | -3.256% |  | No | Yes | Fail | 22500
30 | CBECC-Com 2016.2.1 | 1014506-RetlStrp-WSHP | 176.7 |  | 5.912 |  | 0.063564 |  | 26.5276 |  | 0.68559 |  | 4.0657 |  | 9.9577 |  | 0 |  | 12.4077 |  | 5.5794 |  | 0.51554 |  | 0 |  | 5.7238 |  | 0 |  | 0 |  | 1.8% |  | 0.2547% |  | Yes | Yes | Fail | 22500
| CBECC-Com 2016.2.1 | 1010606-RetlStrp-FPFC | 170.935 |  | 6.0643 |  | 0.064517 |  | 27.1424 |  | 0.72647 |  | 3.3536 |  | 9.9577 |  | 0 |  | 12.4077 |  | 5.744 |  | 1.6263 |  | 0.010617 |  | 5.7238 |  | 0 |  | 0 |  | -1.521% |  | 2.837% |  | No | Yes | Fail | 22500
27 | CBECC-Com 2016.2.1 | 0400016-OffLrg-CRAH | 107.814 |  | 3.3895 |  | 0.099817 |  | 21.5286 |  | 8.7195 |  | 1.5866 |  | 5.1524 |  | 0 |  | 34.2857 |  | 3.5584 |  | 1.2136 |  | 0.036321 |  | 1.2618 |  | 0 |  | 0 | [8 empty] | 498600
5 | CBECC-Com 2016.2.1 | 0413216-OffLrg-CRAC | 112.973 |  | 3.5299 |  | 0.099817 |  | 21.993 |  | 8.7195 |  | 2.162 |  | 5.1524 |  | 0 |  | 34.2857 |  | 3.6407 |  | 1.0339 |  | 0.022601 |  | 1.2618 |  | 0 |  | 0 |  | 4.785% |  | 4.142% |  | Yes | Yes | Fail | 498600
25 | CBECC-Com 2016.2.1 | 0400006-OffLrg-CRAH | 109.082 |  | 3.8508 |  | 0.040313 |  | 17.1412 |  | 2.9504 |  | 3.134 |  | 5.1275 |  | 0 |  | 34.2857 |  | 2.8429 |  | 1.9856 |  | 0.020156 |  | 1.0806 |  | 0 |  | 0 | [8 empty] | 498600
34 | CBECC-Com 2016.2.1 | 0413306-OffLrg-CRAC | 113.584 |  | 4.0112 |  | 0.040311 |  | 17.721 |  | 2.9502 |  | 3.8674 |  | 5.1275 |  | 0 |  | 34.2857 |  | 2.8907 |  | 1.7931 |  | 0.011401 |  | 1.0806 |  | 0 |  | 0 |  | 4.127% |  | 4.167% |  | Yes | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0400007-OffLrg-Baserun | 88.2076 |  | 3.0084 |  | 0.030736 |  | 13.368 |  | 1.9738 |  | 2.1085 |  | 4.996 |  | 0 |  | 14.645 |  | 1.6351 |  | 1.5283 |  | 0.026822 |  | 1.0995 |  | 0 |  | 0 | [8 empty] | 498600
| CBECC-Com 2016.2.1 | 0402507-OffLrg-WWR20 | 86.0194 |  | 2.9884 |  | 0.02847 |  | 13.0101 |  | 1.7472 |  | 1.9409 |  | 5.0804 |  | 0 |  | 14.645 |  | 1.5959 |  | 1.5226 |  | 0.023501 |  | 1.0995 |  | 0 |  | 0 |  | -2.481% |  | -0.6667% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0404207-OffLrg-Cont.DimHighVT | 87.9334 |  | 3.0084 |  | 0.030764 |  | 13.3367 |  | 1.9766 |  | 2.1062 |  | 4.9659 |  | 0 |  | 14.645 |  | 1.6333 |  | 1.5283 |  | 0.026768 |  | 1.0995 |  | 0 |  | 0 |  | -0.3109% |  | 0% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0404307-OffLrg-StepDim | 87.3622 |  | 2.9884 |  | 0.030767 |  | 13.2686 |  | 1.9769 |  | 2.0964 |  | 4.9069 |  | 0 |  | 14.645 |  | 1.6343 |  | 1.5279 |  | 0.026603 |  | 1.0995 |  | 0 |  | 0 |  | -0.9584% |  | -0.6667% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0404407-OffLrg-StepDimHighVT | 87.6659 |  | 2.9683 |  | 0.035312 |  | 13.6712 |  | 2.4314 |  | 2.0622 |  | 4.9069 |  | 0 |  | 14.645 |  | 1.6135 |  | 1.5316 |  | 0.026037 |  | 1.0995 |  | 0 |  | 0 |  | -0.6141% |  | -1.333% |  | No | Yes | Fail | 498600
| CBECC-Com 2016.2.1 | 0500007-RetlMed-Baseline | 172.083 |  | 5.8754 |  | 0.045888 |  | 24.6354 |  | 0.24542 |  | 2.3255 |  | 7.9712 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.3423 |  | 0 |  | 0 | [8 empty] | 24695
| CBECC-Com 2016.2.1 | 0506007-RetlMed-Daylighting SRRBaseHighVT | 169.013 |  | 5.77 |  | 0.045926 |  | 24.2797 |  | 0.24925 |  | 2.3054 |  | 7.6318 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.3423 |  | 0 |  | 0 |  | -1.784% |  | -1.793% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0506107-RetlMed-Daylighting SRR4.67 | 166.414 |  | 5.6311 |  | 0.046314 |  | 23.8446 |  | 0.28799 |  | 2.543 |  | 6.9203 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.3423 |  | 0 |  | 0 |  | -3.294% |  | -4.157% |  | No | Yes | Fail | 24695
| CBECC-Com 2016.2.1 | 0506207-RetlMed-Daylighting SRR4.67HighVT | 166.126 |  | 5.6192 |  | 0.046383 |  | 23.8106 |  | 0.29486 |  | 2.5021 |  | 6.9203 |  | 0 |  | 10.7303 |  | 9.751 |  | 0 |  | 0 |  | 4.3423 |  | 0 |  | 0 |  | -3.462% |  | -4.361% |  | No | Yes | Fail | 24695

## Sheet1 (hidden)
COPY BatchResults.csv values from cell A1 and paste here @cell B2 |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54
|  |  | 4: Analysis:; 8: Proposed Model:; 11: Proposed Model; 23: Proposed Model; 35: Proposed Model; 47: Proposed Model | Proposed Model | [5 empty] | Standard Model: |  |  | Standard Model | [11 empty] | Standard Model | [11 empty] | Standard Model | [11 empty] | Standard Model | [7 empty] | Standard Model | [5 empty] | Calling | Compliance |  |  |  | Secondary
|  |  | 6: Pass /; 7: Compliance; 8: Elapsed; 11: Electric Energy Consumption (kWh); 23: Natural Gas Energy Consumption (therms); 35: Propane Energy Consumption (MBtu); 47: Time Dependent Valuation (kTDV/ft2) | Cooling Unmet Load Hours |  |  | Heating Unmet Load Hours |  |  | Elapsed |  |  | Electric Energy Consumption (kWh) | [11 empty] | Natural Gas Energy Consumption (therms) | [11 empty] | Propane Energy Consumption (MBtu) | [11 empty] | Time Dependent Valuation (kTDV/ft2) | [7 empty] | Cooling Unmet Load Hours |  |  | Heating Unmet Load Hours |  |  | Application | Manager | Ruleset | OpenStudio | EnergyPlus | Simulation
Floor Area | Start Date & Time | Filename (saved to) | Run Title | Weather Station | Analysis Type | Elapsed Time | Fail | Margin | Time | Rule Eval Status | Simulation Status | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Zone Max | Zone Name | Num Zones Exceed Max | Zone Max | Zone Name | Num Zones Exceed Max | Time | Rule Eval Status | Simulation Status | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Lighting | Comp Total | Receptacle | Process | Other Ltg | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Zone Max | Zone Name | Num Zones Exceed Max | Zone Max | Zone Name | Num Zones Exceed Max | Version | Version | Version | Version | Version | Version | Weather File Path | Project Path
| 2016-Sep-19 07:37:52 | 0300006-OffMed-Baseline | 300006 | TORRANCE_722955 | Title24Compliance | 1:22 | PASS | 0.06 | -- | -- | Successful (141 warnings) | 8.3428 | 80517.1 | 22644.6 | 0 | 1718.59 | 0 | 78440.9 | 183329 | 229701 | 0 | 0 | 413031 | 1282.23 | 0 | 0 | 0 | 0 | 609.051 | 0 | 1891.28 | 0 | 0 | 0 | 1891.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 54.6751 | 10.8879 | 0 | 0.54249 | 1.6342 | 36.1243 | 107.797 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:39:31 | 0300016-OffMed-Baseline | 300016 | BLUE-CANYON_725845 | Title24Compliance | 1:34 | PASS | 1.41 | -- | -- | Successful (141 warnings) | 39.3493 | 44721.7 | 26392.8 | 0 | 4253.23 | 0 | 78429.8 | 153837 | 229701 | 0 | 0 | 383538 | 6047.71 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6757.18 | 0 | 0 | 0 | 6757.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1992 | 38.9764 | 12.9864 | 0 | 1.3342 | 1.909 | 35.6559 | 109.061 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:41:09 | 0301516-OffMed-FloorSlabInsulation | 301516 | BLUE-CANYON_725845 | Title24Compliance | 1:34 | PASS | 1.57 | -- | -- | Successful (141 warnings) | 38.4014 | 44970.5 | 26553 | 0 | 4200.54 | 0 | 78429.8 | 154192 | 229701 | 0 | 0 | 383894 | 5902.02 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6611.49 | 0 | 0 | 0 | 6611.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.7605 | 39.1785 | 13.0774 | 0 | 1.3178 | 1.909 | 35.6559 | 108.899 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:42:44 | 0301716-OffMed-GlazingWindowU | 301716 | BLUE-CANYON_725845 | Title24Compliance | 1:29 | PASS | 2.62 | -- | -- | Successful (141 warnings) | 36.0859 | 45080.1 | 26648.3 | 0 | 4078.72 | 0 | 78433.1 | 154276 | 229701 | 0 | 0 | 383978 | 5546.15 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6255.63 | 0 | 0 | 0 | 6255.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7116 | 39.1906 | 13.109 | 0 | 1.2804 | 1.909 | 35.6572 | 107.858 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:44:16 | 0301816-OffMed-GlazingWindowSHGC | 301816 | BLUE-CANYON_725845 | Title24Compliance | 1:28 | PASS | 2.73 | -- | -- | Successful (141 warnings) | 41.5111 | 42715.3 | 25393.5 | 0 | 4446.23 | 0 | 78429.8 | 151026 | 229701 | 0 | 0 | 380728 | 6379.96 | 0 | 0 | 0 | 0 | 709.475 | 0 | 7089.44 | 0 | 0 | 0 | 7089.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1617 | 37.2173 | 12.4025 | 0 | 1.3953 | 1.909 | 35.6559 | 107.742 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:45:48 | 0301916-OffMed-GlazingWindowUSHGC | 301916 | BLUE-CANYON_725845 | Title24Compliance | 1:28 | PASS | 4.03 | -- | -- | Successful (141 warnings) | 38.1425 | 43033.8 | 25576.5 | 0 | 4257.26 | 0 | 78433.1 | 151339 | 229701 | 0 | 0 | 381040 | 5862.23 | 0 | 0 | 0 | 0 | 709.474 | 0 | 6571.7 | 0 | 0 | 0 | 6571.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6303 | 37.4098 | 12.5005 | 0 | 1.3368 | 1.909 | 35.6572 | 106.444 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:47:08 | 0302006-OffMed-FloorSlabInsulation | 302006 | TORRANCE_722955 | Title24Compliance | 1:15 | FAIL | -0.17 | -- | -- | Successful (141 warnings) | 8.0948 | 80922.7 | 22758.2 | 0 | 1677.71 | 0 | 78440.9 | 183808 | 229701 | 0 | 0 | 413509 | 1244.11 | 0 | 0 | 0 | 0 | 609.051 | 0 | 1853.17 | 0 | 0 | 0 | 1853.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8169 | 54.9614 | 10.9624 | 0 | 0.52902 | 1.6342 | 36.1243 | 108.028 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:48:27 | 0302206-OffMed-GlazingWindowU | 302206 | TORRANCE_722955 | Title24Compliance | 1:14 | PASS | 0.07 | -- | -- | Successful (141 warnings) | 7.334 | 81298.2 | 22939.1 | 0 | 1611.66 | 0 | 78443.4 | 184300 | 229701 | 0 | 0 | 414001 | 1127.19 | 0 | 0 | 0 | 0 | 609.05 | 0 | 1736.24 | 0 | 0 | 0 | 1736.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4713 | 55.0303 | 11.0099 | 0 | 0.50801 | 1.6342 | 36.1254 | 107.779 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:49:48 | 0302306-OffMed-GlazingWindowSHGC | 302306 | TORRANCE_722955 | Title24Compliance | 1:15 | PASS | 2.4 | -- | -- | Successful (141 warnings) | 9.2826 | 77145.4 | 21633.5 | 0 | 1849.83 | 0 | 78440.9 | 179079 | 229701 | 0 | 0 | 408780 | 1426.67 | 0 | 0 | 0 | 0 | 609.05 | 0 | 2035.72 | 0 | 0 | 0 | 2035.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3557 | 52.4666 | 10.2949 | 0 | 0.58486 | 1.6342 | 36.1243 | 105.461 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:51:07 | 0302406-OffMed-GlazingWindowUSHGC | 302406 | TORRANCE_722955 | Title24Compliance | 1:15 | PASS | 2.5 | -- | -- | Successful (141 warnings) | 8.1906 | 77840.2 | 21881.8 | 0 | 1738.83 | 0 | 78443.4 | 179912 | 229701 | 0 | 0 | 409614 | 1258.84 | 0 | 0 | 0 | 0 | 609.05 | 0 | 1867.89 | 0 | 0 | 0 | 1867.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.858 | 52.7815 | 10.3962 | 0 | 0.54893 | 1.6342 | 36.1254 | 105.344 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:52:40 | 0303216-OffMed-LightingLowLPD | 303216 | BLUE-CANYON_725845 | Title24Compliance | 1:28 | PASS | 9.06 | -- | -- | Successful (141 warnings) | 40.8796 | 43817.9 | 25796.7 | 0 | 4382.99 | 0 | 62743.9 | 136782 | 229701 | 0 | 0 | 366484 | 6282.9 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6992.38 | 0 | 0 | 0 | 6992.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8893 | 38.1414 | 12.577 | 0 | 1.3752 | 1.909 | 28.5248 | 101.417 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:54:12 | 0303316-OffMed-LightingHighLPD | 303316 | BLUE-CANYON_725845 | Title24Compliance | 1:28 | FAIL | -6.28 | -- | -- | Successful (141 warnings) | 37.8588 | 45641 | 27039.1 | 0 | 4140.63 | 0 | 94115.8 | 170974 | 229701 | 0 | 0 | 400676 | 5818.64 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6528.11 | 0 | 0 | 0 | 6528.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5244 | 39.8249 | 13.4193 | 0 | 1.2991 | 1.909 | 42.7871 | 116.764 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:55:32 | 0303406-OffMed-LightingLowLPD | 303406 | TORRANCE_722955 | Title24Compliance | 1:15 | PASS | 8.61 | -- | -- | Successful (141 warnings) | 9.0079 | 78549.5 | 21990.9 | 0 | 1811.96 | 0 | 62752.7 | 165114 | 229701 | 0 | 0 | 394815 | 1384.46 | 0 | 0 | 0 | 0 | 609.051 | 0 | 1993.51 | 0 | 0 | 0 | 1993.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2333 | 53.4068 | 10.4966 | 0 | 0.57267 | 1.6342 | 28.8994 | 99.243 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:56:53 | 0303506-OffMed-LightingHighLPD | 303506 | TORRANCE_722955 | Title24Compliance | 1:16 | FAIL | -8.56 | -- | -- | Successful (141 warnings) | 7.7385 | 82501.5 | 23349.3 | 0 | 1634.3 | 0 | 94129.1 | 201622 | 229701 | 0 | 0 | 431323 | 1189.35 | 0 | 0 | 0 | 0 | 609.051 | 0 | 1798.4 | 0 | 0 | 0 | 1798.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.66 | 55.953 | 11.3025 | 0 | 0.51527 | 1.6342 | 43.3491 | 116.414 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 07:58:27 | 0307216-OffMed-HVACPVAV Design | 307216 | BLUE-CANYON_725845 | Title24Compliance | 1:29 | PASS | 5.3 | -- | -- | Successful (141 warnings) | 39.9257 | 43851 | 19189.2 | 0 | 4273.6 | 0 | 78429.8 | 145783 | 229701 | 0 | 0 | 375485 | 6136.29 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6845.77 | 0 | 0 | 0 | 6845.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4643 | 38.3745 | 9.4422 | 0 | 1.3406 | 1.909 | 35.6559 | 105.187 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:00:23 | 0307316-OffMed-HVACPVAV SATControl | 307316 | BLUE-CANYON_725845 | Title24Compliance | 1:51 | FAIL | -7.41 | -- | -- | Successful (141 warnings) | 49.9574 | 64723 | 23010.6 | 0 | 5123.9 | 0 | 78429.8 | 171337 | 229701 | 0 | 0 | 401039 | 7678.09 | 0 | 0 | 0 | 0 | 709.477 | 0 | 8387.57 | 0 | 0 | 0 | 8387.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2236 | 46.7774 | 9.6382 | 0 | 1.6844 | 1.909 | 35.6559 | 117.889 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:01:55 | 0307516-OffMed-HVACPVAV EconomizerType | 307516 | BLUE-CANYON_725845 | Title24Compliance | 1:28 | PASS | 1.24 | -- | -- | Successful (141 warnings) | 39.3489 | 45270.7 | 26397 | 0 | 4253.08 | 0 | 78429.8 | 154390 | 229701 | 0 | 0 | 384091 | 6047.65 | 0 | 0 | 0 | 0 | 709.475 | 0 | 6757.13 | 0 | 0 | 0 | 6757.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1991 | 39.1488 | 12.9884 | 0 | 1.3341 | 1.909 | 35.6559 | 109.235 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:03:16 | 0307606-OffMed-HVACPVAV Design | 307606 | TORRANCE_722955 | Title24Compliance | 1:16 | PASS | 3.78 | -- | -- | Successful (141 warnings) | 8.4833 | 78911.8 | 16462.8 | 0 | 1725.59 | 0 | 78440.9 | 175550 | 229701 | 0 | 0 | 405251 | 1303.82 | 0 | 0 | 0 | 0 | 609.051 | 0 | 1912.87 | 0 | 0 | 0 | 1912.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0002 | 53.8578 | 7.9158 | 0 | 0.54474 | 1.6342 | 36.1243 | 104.077 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:04:40 | 0307706-OffMed-HVACPVAV SATControl | 307706 | TORRANCE_722955 | Title24Compliance | 1:19 | FAIL | -24.08 | -- | -- | Successful (141 warnings) | 25.7698 | 135689 | 17512.6 | 0 | 2938.81 | 0 | 78440.9 | 234607 | 229701 | 0 | 0 | 464308 | 3960.65 | 0 | 0 | 0 | 0 | 609.052 | 0 | 4569.7 | 0 | 0 | 0 | 4569.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8994 | 74.7854 | 7.4993 | 0 | 0.98759 | 1.6342 | 36.1243 | 131.93 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:06:00 | 0307906-OffMed-HVACPVAV EconomizerType | 307906 | TORRANCE_722955 | Title24Compliance | 1:15 | PASS | 0.95 | -- | -- | Successful (141 warnings) | 8.3425 | 79394.8 | 22657 | 0 | 1718.07 | 0 | 78440.9 | 182219 | 229701 | 0 | 0 | 411920 | 1282.2 | 0 | 0 | 0 | 0 | 609.051 | 0 | 1891.25 | 0 | 0 | 0 | 1891.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 53.7753 | 10.8952 | 0 | 0.54233 | 1.6342 | 36.1243 | 106.905 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:07:33 | 0312616-OffMed-Plenum | 312616 | BLUE-CANYON_725845 | Title24Compliance | 1:28 | PASS | 2.9 | -- | -- | Successful (141 warnings) | 38.7229 | 43993.6 | 25650.7 | 0 | 4422.94 | 0 | 78429.8 | 152536 | 229701 | 0 | 0 | 382237 | 5951.44 | 0 | 0 | 0 | 0 | 709.472 | 0 | 6660.92 | 0 | 0 | 0 | 6660.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8479 | 38.5464 | 12.2153 | 0 | 1.3894 | 1.909 | 35.6559 | 107.564 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:08:52 | 0312706-OffMed-Plenum | 312706 | TORRANCE_722955 | Title24Compliance | 1:14 | PASS | 1.01 | -- | -- | Successful (141 warnings) | 8.9381 | 79003.8 | 21761.6 | 0 | 1884.88 | 0 | 78440.9 | 181100 | 229701 | 0 | 0 | 410802 | 1373.73 | 0 | 0 | 0 | 0 | 609.048 | 0 | 1982.78 | 0 | 0 | 0 | 1982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1575 | 54.1622 | 10.1684 | 0 | 0.5967 | 1.6342 | 36.1243 | 106.843 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:10:33 | 0313516-OffMed-LabwExhDOAS | 313516 | BLUE-CANYON_725845 | Title24Compliance | 1:36 | FAIL | -72.44 | -- | -- | Successful (142 warnings) | 279.764 | 49554 | 207502 | 0 | 9618.75 | 0 | 115458 | 382412 | 235375 | 23370.4 | 0 | 641158 | 42997.9 | 0 | 0 | 0 | 0 | 717.135 | 0 | 43715.1 | 2888.07 | 0 | 0 | 46603.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.898 | 48.3419 | 81.2899 | 0 | 2.9841 | 1.93 | 51.9893 | 313.434 | [6 empty] | -- | -- | Successful (133 warnings) | 155.752 | 62857.6 | 137275 | 0 | 10305.9 | 0 | 110368 | 320963 | 235375 | 23370.4 | 0 | 579708 | 25310.9 | 0 | 0 | 0 | 0 | 748.53 | 0 | 26059.4 | 2888.07 | 0 | 0 | 28947.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6792 | 52.9557 | 59.1507 | 0 | 3.7338 | 2.0141 | 49.4624 | 240.996 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:12:02 | 0313606-OffMed-LabwExhDOAS | 313606 | TORRANCE_722955 | Title24Compliance | 1:24 | FAIL | -21.72 | -- | -- | Successful (140 warnings) | 129.502 | 83128.1 | 199788 | 0 | 7908.32 | 0 | 115469 | 406423 | 235375 | 23370.4 | 0 | 665169 | 19903.6 | 0 | 0 | 0 | 0 | 615.569 | 0 | 20519.2 | 2888.07 | 0 | 0 | 23407.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.0372 | 66.7402 | 78.6935 | 0 | 2.4698 | 1.6519 | 52.5132 | 261.106 | [6 empty] | -- | -- | Successful (125 warnings) | 81.2954 | 133069 | 134779 | 0 | 8526.1 | 0 | 109803 | 386259 | 235375 | 23370.4 | 0 | 645005 | 14452.1 | 0 | 0 | 0 | 0 | 646.949 | 0 | 15099.1 | 2888.07 | 0 | 0 | 17987.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7322 | 86.4912 | 57.4923 | 0 | 3.2477 | 1.7361 | 49.6848 | 239.384 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:13:38 | 0314116-OffMed-FanPwrBox | 314116 | BLUE-CANYON_725845 | Title24Compliance | 1:32 | FAIL | -27.54 | -- | -- | Successful (141 warnings) | 30.7202 | 48233.2 | 103261 | 0 | 2706.09 | 0 | 78429.8 | 232661 | 229701 | 0 | 0 | 462362 | 4721.48 | 0 | 0 | 0 | 0 | 709.473 | 0 | 5430.95 | 0 | 0 | 0 | 5430.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2992 | 41.8619 | 43.4361 | 0 | 0.84806 | 1.909 | 35.6559 | 138.01 | [6 empty] | -- | -- | Successful (134 warnings) | 40.71 | 40364.8 | 38498.1 | 0 | 2869.95 | 0 | 73340.1 | 155114 | 229701 | 0 | 0 | 384815 | 6659.98 | 0 | 0 | 0 | 0 | 740.874 | 0 | 7400.85 | 0 | 0 | 0 | 7400.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0133 | 35.7014 | 18.7543 | 0 | 0.89958 | 1.9932 | 33.129 | 110.491 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:14:59 | 0314206-OffMed-FanPwrBox | 314206 | TORRANCE_722955 | Title24Compliance | 1:16 | FAIL | -23.39 | -- | -- | Successful (141 warnings) | 5.2235 | 85784 | 77234.1 | 0 | 929.747 | 0 | 78440.9 | 242394 | 229701 | 0 | 0 | 472095 | 802.817 | 0 | 0 | 0 | 0 | 609.049 | 0 | 1411.87 | 0 | 0 | 0 | 1411.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5168 | 57.9386 | 32.7448 | 0 | 0.29419 | 1.6342 | 36.1243 | 131.253 | [6 empty] | -- | -- | Successful (128 warnings) | 9.4745 | 75404.4 | 35578.7 | 0 | 1376.62 | 0 | 72774.6 | 185144 | 229701 | 0 | 0 | 414845 | 1666.48 | 0 | 0 | 0 | 0 | 640.432 | 0 | 2306.91 | 0 | 0 | 0 | 2306.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1091 | 50.3223 | 16.9611 | 0 | 0.43538 | 1.7183 | 33.2959 | 107.842 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:16:42 | 0314716-OffMed-LabwExhPVAV | 314716 | BLUE-CANYON_725845 | Title24Compliance | 1:38 | FAIL | -81.93 | -- | -- | Successful (141 warnings) | 292.632 | 90849 | 160727 | 0 | 18289.4 | 0 | 115458 | 385616 | 235375 | 23370.4 | 0 | 644361 | 44975.6 | 0 | 0 | 0 | 0 | 717.135 | 0 | 45692.7 | 2888.07 | 0 | 0 | 48580.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.752 | 68.6221 | 63.6811 | 0 | 6.9516 | 1.93 | 51.9893 | 322.926 | [6 empty] | -- | -- | Successful (133 warnings) | 155.752 | 62857.6 | 137275 | 0 | 10305.9 | 0 | 110368 | 320963 | 235375 | 23370.4 | 0 | 579708 | 25310.9 | 0 | 0 | 0 | 0 | 748.53 | 0 | 26059.4 | 2888.07 | 0 | 0 | 28947.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6792 | 52.9557 | 59.1507 | 0 | 3.7338 | 2.0141 | 49.4624 | 240.996 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:18:11 | 0314806-OffMed-LabwExhPVAV | 314806 | TORRANCE_722955 | Title24Compliance | 1:24 | FAIL | -75.14 | -- | -- | Successful (141 warnings) | 181.568 | 191737 | 158068 | 0 | 17058.9 | 0 | 115469 | 482514 | 235375 | 23370.4 | 0 | 741260 | 27905.8 | 0 | 0 | 0 | 0 | 615.569 | 0 | 28521.3 | 2888.07 | 0 | 0 | 31409.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8755 | 113.343 | 62.6567 | 0 | 6.477 | 1.6519 | 52.5132 | 314.517 | [6 empty] | -- | -- | Successful (125 warnings) | 81.2954 | 133069 | 134779 | 0 | 8526.1 | 0 | 109803 | 386259 | 235375 | 23370.4 | 0 | 645005 | 14452.1 | 0 | 0 | 0 | 0 | 646.949 | 0 | 15099.1 | 2888.07 | 0 | 0 | 17987.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.7322 | 86.4912 | 57.4923 | 0 | 3.2477 | 1.7361 | 49.6848 | 239.384 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:21:23 | 0400006-OffLrg-Baserun | 400006 | TORRANCE_722955 | Title24Compliance | 3:08 | PASS | 0.99 | -- | -- | Successful (152 warnings) | 106.546 | 350725 | 249674 | 2156.07 | 229376 | 0 | 728541 | 1560000 | 2140000 | 0 | 0 | 3700000 | 16375.5 | 0 | 0 | 0 | 0 | 5569.04 | 0 | 21944.5 | 0 | 0 | 0 | 21944.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.133 | 26.0402 | 12.4039 | 0.27062 | 11.0682 | 1.6073 | 36.041 | 92.5642 | [6 empty] | -- | -- | Successful (152 warnings) | 92.3874 | 280973 | 393229 | 38933.5 | 100071 | 0 | 728544 | 1540000 | 2140000 | 0 | 0 | 3680000 | 15755.3 | 0 | 0 | 0 | 0 | 5567.43 | 0 | 21322.8 | 0 | 0 | 0 | 21322.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0254 | 22.3093 | 20.0324 | 3.0082 | 5.5219 | 1.6068 | 36.0411 | 93.5451 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:25:00 | 0400006-OffLrg-CRAH | 400006 | TORRANCE_722955 | Title24Compliance | 3:31 | PASS | 1.38 | -- | -- | Successful (152 warnings) | 95.7162 | 457950 | 415422 | 2945.34 | 290148 | 0 | 749261 | 1920000 | 5010000 | 0 | 0 | 6920000 | 14710.9 | 0 | 0 | 0 | 0 | 5389.25 | 0 | 20100.2 | 0 | 0 | 0 | 20100.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6133 | 32.4327 | 19.3803 | 0.33282 | 13.6874 | 1.5553 | 37.0799 | 109.082 | [6 empty] | -- | -- | Successful (152 warnings) | 81.169 | 489346 | 501984 | 37457.3 | 95844.7 | 0 | 749263 | 1870000 | 5010000 | 0 | 0 | 6880000 | 14047.8 | 0 | 0 | 0 | 0 | 5387.7 | 0 | 19435.5 | 0 | 0 | 0 | 19435.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4822 | 34.7993 | 24.3665 | 2.8893 | 5.2891 | 1.5549 | 37.08 | 110.461 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:28:22 | 0400007-OffLrg-Baserun | 400007 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 3:17 | PASS | 2.07 | -- | -- | Successful (148 warnings) | 64.0322 | 308111 | 238926 | 3919.33 | 223320 | 0 | 730044 | 1500000 | 2140000 | 0 | 0 | 3640000 | 9841.31 | 0 | 0 | 0 | 0 | 5483.45 | 0 | 15324.8 | 0 | 0 | 0 | 15324.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1086 | 23.875 | 11.8975 | 0.49997 | 10.7793 | 1.5939 | 36.4535 | 88.2076 | [6 empty] | -- | -- | Successful (148 warnings) | 57.0037 | 244317 | 397767 | 30239.8 | 98669.5 | 0 | 730046 | 1500000 | 2140000 | 0 | 0 | 3640000 | 9852.81 | 0 | 0 | 0 | 0 | 5481.98 | 0 | 15334.8 | 0 | 0 | 0 | 15334.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1055 | 20.77 | 20.3157 | 2.5718 | 5.4684 | 1.5934 | 36.4536 | 90.2785 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:32:27 | 0400016-OffLrg-Baserun | 400016 | BLUE-CANYON_725845 | Title24Compliance | 4:00 | PASS | 4.54 | -- | -- | Successful (152 warnings) | 311.597 | 167904 | 273717 | 3770.62 | 135736 | 0 | 732179 | 1310000 | 2140000 | 0 | 0 | 3450000 | 47890.4 | 0 | 0 | 0 | 0 | 6502.78 | 0 | 54393.2 | 0 | 0 | 0 | 54393.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3957 | 15.1647 | 13.7537 | 0.56703 | 7.8187 | 1.8821 | 35.7803 | 90.3622 | [6 empty] | -- | -- | Successful (156 warnings) | 308.394 | 146188 | 428879 | 7289.85 | 64756.7 | 0 | 732182 | 1380000 | 2140000 | 0 | 0 | 3520000 | 49729.3 | 0 | 0 | 0 | 0 | 6501.14 | 0 | 56230.4 | 0 | 0 | 0 | 56230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.9083 | 14.5707 | 22.033 | 0.91608 | 3.8085 | 1.8816 | 35.7804 | 94.8986 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:36:43 | 0400016-OffLrg-CRAH | 400016 | BLUE-CANYON_725845 | Title24Compliance | 4:10 | PASS | 2.61 | -- | -- | Successful (153 warnings) | 282.877 | 231836 | 519977 | 5307.44 | 177339 | 0 | 752899 | 1690000 | 5010000 | 0 | 0 | 6700000 | 43476.3 | 0 | 0 | 0 | 0 | 6292.6 | 0 | 49768.8 | 0 | 0 | 0 | 49768.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9911 | 20.1219 | 24.5018 | 0.74521 | 9.8144 | 1.8213 | 36.8185 | 107.814 | [6 empty] | -- | -- | Successful (158 warnings) | 279.085 | 278889 | 563425 | 7037.25 | 60568.3 | 0 | 752901 | 1660000 | 5010000 | 0 | 0 | 6670000 | 45036.2 | 0 | 0 | 0 | 0 | 6291.06 | 0 | 51327.3 | 0 | 0 | 0 | 51327.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4233 | 25.0317 | 27.8368 | 0.87341 | 3.6185 | 1.8208 | 36.8186 | 110.423 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:39:53 | 0402507-OffLrg-WWR20 | 402507 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 3:05 | PASS | 0.08 | -- | -- | Successful (148 warnings) | 56.6827 | 283619 | 233194 | 3434.07 | 222493 | 0 | 742381 | 1490000 | 2140000 | 0 | 0 | 3620000 | 8711.74 | 0 | 0 | 0 | 0 | 5483.43 | 0 | 14195.2 | 0 | 0 | 0 | 14195.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7394 | 21.7205 | 11.7174 | 0.43979 | 10.7125 | 1.5939 | 37.0959 | 86.0194 | [6 empty] | -- | -- | Successful (148 warnings) | 41.4686 | 225178 | 361386 | 28518.4 | 95094.4 | 0 | 742381 | 1450000 | 2140000 | 0 | 0 | 3590000 | 7100.49 | 0 | 0 | 0 | 0 | 5481.97 | 0 | 12582.5 | 0 | 0 | 0 | 12582.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2682 | 19.1801 | 18.2456 | 2.4722 | 5.2397 | 1.5934 | 37.0959 | 86.0951 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:42:30 | 0404207-OffLrg-Cont.DimHighVT | 404207 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 2:32 | PASS | 2.36 | -- | -- | Successful (148 warnings) | 64.1243 | 307776 | 238670 | 3911.49 | 223324 | 0 | 725647 | 1500000 | 2140000 | 0 | 0 | 3630000 | 9855.46 | 0 | 0 | 0 | 0 | 5483.45 | 0 | 15338.9 | 0 | 0 | 0 | 15338.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1127 | 23.8417 | 11.8826 | 0.49905 | 10.7787 | 1.5939 | 36.2248 | 87.9334 | [6 empty] | -- | -- | Successful (148 warnings) | 57.0037 | 244317 | 397767 | 30239.8 | 98669.5 | 0 | 730046 | 1500000 | 2140000 | 0 | 0 | 3640000 | 9852.81 | 0 | 0 | 0 | 0 | 5481.98 | 0 | 15334.8 | 0 | 0 | 0 | 15334.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1055 | 20.77 | 20.3157 | 2.5718 | 5.4684 | 1.5934 | 36.4536 | 90.2785 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:45:59 | 0404307-OffLrg-StepDim | 404307 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 3:23 | PASS | 2.92 | -- | -- | Successful (148 warnings) | 64.1336 | 306341 | 238812 | 3887.3 | 223267 | 0 | 717028 | 1490000 | 2140000 | 0 | 0 | 3620000 | 9856.89 | 0 | 0 | 0 | 0 | 5483.45 | 0 | 15340.3 | 0 | 0 | 0 | 15340.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1132 | 23.7158 | 11.9047 | 0.4961 | 10.7725 | 1.5939 | 35.766 | 87.3622 | [6 empty] | -- | -- | Successful (148 warnings) | 57.0037 | 244317 | 397767 | 30239.8 | 98669.5 | 0 | 730046 | 1500000 | 2140000 | 0 | 0 | 3640000 | 9852.81 | 0 | 0 | 0 | 0 | 5481.98 | 0 | 15334.8 | 0 | 0 | 0 | 15334.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1055 | 20.77 | 20.3157 | 2.5718 | 5.4684 | 1.5934 | 36.4536 | 90.2785 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:49:08 | 0404407-OffLrg-StepDimHighVT | 404407 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 3:05 | PASS | 2.6 | -- | -- | Successful (148 warnings) | 78.8792 | 301335 | 235779 | 3804.63 | 223801 | 0 | 717028 | 1480000 | 2140000 | 0 | 0 | 3620000 | 12123.2 | 0 | 0 | 0 | 0 | 5483.45 | 0 | 17606.6 | 0 | 0 | 0 | 17606.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8158 | 23.4273 | 11.7851 | 0.48941 | 10.7883 | 1.5939 | 35.766 | 87.6659 | [6 empty] | -- | -- | Successful (148 warnings) | 57.0037 | 244317 | 397767 | 30239.8 | 98669.5 | 0 | 730046 | 1500000 | 2140000 | 0 | 0 | 3640000 | 9852.81 | 0 | 0 | 0 | 0 | 5481.98 | 0 | 15334.8 | 0 | 0 | 0 | 15334.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1055 | 20.77 | 20.3157 | 2.5718 | 5.4684 | 1.5934 | 36.4536 | 90.2785 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:52:27 | 0408416-OffLrg-HVACChillerCOP | 408416 | BLUE-CANYON_725845 | Title24Compliance | 3:14 | PASS | 7.89 | -- | -- | Successful (152 warnings) | 311.597 | 133181 | 273717 | 3699.34 | 132308 | 0 | 732179 | 1280000 | 2140000 | 0 | 0 | 3410000 | 47890.4 | 0 | 0 | 0 | 0 | 6502.78 | 0 | 54393.2 | 0 | 0 | 0 | 54393.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3957 | 12.0283 | 13.7537 | 0.55552 | 7.6136 | 1.8821 | 35.7803 | 87.0093 | [6 empty] | -- | -- | Successful (156 warnings) | 308.394 | 146188 | 428879 | 7289.85 | 64756.7 | 0 | 732182 | 1380000 | 2140000 | 0 | 0 | 3520000 | 49729.3 | 0 | 0 | 0 | 0 | 6501.14 | 0 | 56230.4 | 0 | 0 | 0 | 56230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.9083 | 14.5707 | 22.033 | 0.91608 | 3.8085 | 1.8816 | 35.7804 | 94.8986 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:55:43 | 0408516-OffLrg-HVACChWdeltaT | 408516 | BLUE-CANYON_725845 | Title24Compliance | 3:11 | PASS | 5.92 | -- | -- | Successful (152 warnings) | 311.596 | 156913 | 273811 | 3644.58 | 135916 | 0 | 732179 | 1300000 | 2140000 | 0 | 0 | 3440000 | 47890.3 | 0 | 0 | 0 | 0 | 6502.78 | 0 | 54393.1 | 0 | 0 | 0 | 54393.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3957 | 13.8196 | 13.7643 | 0.55583 | 7.7792 | 1.8821 | 35.7803 | 88.977 | [6 empty] | -- | -- | Successful (156 warnings) | 308.394 | 146188 | 428879 | 7289.85 | 64756.7 | 0 | 732182 | 1380000 | 2140000 | 0 | 0 | 3520000 | 49729.3 | 0 | 0 | 0 | 0 | 6501.14 | 0 | 56230.4 | 0 | 0 | 0 | 56230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.9083 | 14.5707 | 22.033 | 0.91608 | 3.8085 | 1.8816 | 35.7804 | 94.8986 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 08:58:52 | 0408806-OffLrg-HVACChillerCOP | 408806 | TORRANCE_722955 | Title24Compliance | 3:04 | PASS | 6.69 | -- | -- | Successful (152 warnings) | 106.546 | 278214 | 249674 | 2113.45 | 223016 | 0 | 728541 | 1480000 | 2140000 | 0 | 0 | 3620000 | 16375.5 | 0 | 0 | 0 | 0 | 5569.04 | 0 | 21944.5 | 0 | 0 | 0 | 21944.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.133 | 20.6554 | 12.4039 | 0.26423 | 10.7622 | 1.6073 | 36.041 | 86.867 | [6 empty] | -- | -- | Successful (152 warnings) | 92.3874 | 280973 | 393229 | 38933.5 | 100071 | 0 | 728544 | 1540000 | 2140000 | 0 | 0 | 3680000 | 15755.3 | 0 | 0 | 0 | 0 | 5567.43 | 0 | 21322.8 | 0 | 0 | 0 | 21322.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0254 | 22.3093 | 20.0324 | 3.0082 | 5.5219 | 1.6068 | 36.0411 | 93.5451 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:02:00 | 0408906-OffLrg-HVACChWdeltaT | 408906 | TORRANCE_722955 | Title24Compliance | 3:04 | PASS | 5.08 | -- | -- | Successful (152 warnings) | 106.559 | 304324 | 249551 | 1862.54 | 229980 | 0 | 728541 | 1510000 | 2140000 | 0 | 0 | 3650000 | 16377.4 | 0 | 0 | 0 | 0 | 5569.04 | 0 | 21946.5 | 0 | 0 | 0 | 21946.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1335 | 21.9916 | 12.3922 | 0.24749 | 11.0606 | 1.6073 | 36.041 | 88.4736 | [6 empty] | -- | -- | Successful (152 warnings) | 92.3874 | 280973 | 393229 | 38933.5 | 100071 | 0 | 728544 | 1540000 | 2140000 | 0 | 0 | 3680000 | 15755.3 | 0 | 0 | 0 | 0 | 5567.43 | 0 | 21322.8 | 0 | 0 | 0 | 21322.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0254 | 22.3093 | 20.0324 | 3.0082 | 5.5219 | 1.6068 | 36.0411 | 93.5451 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:06:15 | 0413216-OffLrg-CRAC | 413216 | BLUE-CANYON_725845 | Title24Compliance | 4:10 | FAIL | -2.55 | -- | -- | Successful (157 warnings) | 282.878 | 315925 | 532002 | 3302.57 | 151079 | 0 | 752899 | 1760000 | 5010000 | 0 | 0 | 6760000 | 43476.4 | 0 | 0 | 0 | 0 | 6292.6 | 0 | 49769 | 0 | 0 | 0 | 49769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9911 | 26.0472 | 25.0314 | 0.52062 | 8.7427 | 1.8213 | 36.8185 | 112.973 | [6 empty] | -- | -- | Successful (158 warnings) | 279.085 | 278889 | 563425 | 7037.25 | 60568.3 | 0 | 752901 | 1660000 | 5010000 | 0 | 0 | 6670000 | 45036.2 | 0 | 0 | 0 | 0 | 6291.06 | 0 | 51327.3 | 0 | 0 | 0 | 51327.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4233 | 25.0317 | 27.8368 | 0.87341 | 3.6185 | 1.8208 | 36.8186 | 110.423 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:10:39 | 0413306-OffLrg-CRAC | 413306 | TORRANCE_722955 | Title24Compliance | 4:19 | FAIL | -3.13 | -- | -- | Successful (156 warnings) | 95.71 | 565128 | 422409 | 1666.04 | 262016 | 0 | 749261 | 2000000 | 5010000 | 0 | 0 | 7010000 | 14710 | 0 | 0 | 0 | 0 | 5389.25 | 0 | 20099.2 | 0 | 0 | 0 | 20099.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6131 | 37.9871 | 19.5215 | 0.23041 | 12.5969 | 1.5553 | 37.0799 | 113.584 | [6 empty] | -- | -- | Successful (152 warnings) | 81.169 | 489346 | 501984 | 37457.3 | 95844.7 | 0 | 749263 | 1870000 | 5010000 | 0 | 0 | 6880000 | 14047.8 | 0 | 0 | 0 | 0 | 5387.7 | 0 | 19435.5 | 0 | 0 | 0 | 19435.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4822 | 34.7993 | 24.3665 | 2.8893 | 5.2891 | 1.5549 | 37.08 | 110.461 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-23 14:53:04 | 0500006-RetlMed-Baseline | 500006 | TORRANCE_722955 | Title24Compliance | 1:51 | FAIL | -34.97 | -- | -- | Successful (90 warnings) | 0 | 25456 | 70571.5 | 0 | 0 | 0 | 56247.6 | 152275 | 77659.4 | 0 | 200.149 | 230135 | 135.777 | 0 | 0 | 0 | 0 | 1089.28 | 0 | 1225.06 | 0 | 0 | 0 | 1225.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92837 | 47.9798 | 67.0059 | 0 | 0 | 6.3883 | 54.5895 | 176.892 | [6 empty] | -- | -- | Successful (80 warnings) | 4.0616 | 40595.1 | 16022.7 | 0 | 1179.99 | 0 | 53875.9 | 111678 | 77659.4 | 0 | 424.5 | 189762 | 704.785 | 0 | 0 | 0 | 0 | 1178.96 | 0 | 1883.74 | 0 | 0 | 0 | 1883.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8278 | 61.2176 | 15.998 | 0 | 0.82784 | 6.914 | 52.1423 | 141.928 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160923_2016_SST_DG\
| 2016-Sep-22 22:57:12 | 0500007-RetlMed-Baseline | 500007 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 2:02 | FAIL | -35.26 | -- | -- | Successful (90 warnings) | 0 | 16830.7 | 70571.5 | 0 | 0 | 0 | 57690.5 | 145093 | 77659.4 | 0 | 201.456 | 222954 | 60.6203 | 0 | 0 | 0 | 0 | 1072.59 | 0 | 1133.21 | 0 | 0 | 0 | 1133.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.413 | 39.1352 | 68.0278 | 0 | 0 | 6.3358 | 58.171 | 172.083 | [6 empty] | -- | -- | Successful (81 warnings) | 2.2438 | 34019 | 15831.4 | 0 | 876.154 | 0 | 55436.3 | 106165 | 77659.4 | 0 | 424.5 | 184249 | 397.115 | 0 | 0 | 0 | 0 | 1161.21 | 0 | 1558.32 | 0 | 0 | 0 | 1558.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7547 | 54.5928 | 16.0599 | 0 | 0.62895 | 6.8592 | 55.9374 | 136.833 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 22:59:21 | 0500015-RetlMed-Baseline | 500015 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 2:05 | FAIL | -28.57 | -- | -- | Successful (92 warnings) | 0 | 97376.5 | 73371 | 0 | 0 | 0 | 58788 | 229535 | 77659.4 | 0 | 202.152 | 307397 | 82.2661 | 0 | 0 | 0 | 0 | 943.578 | 0 | 1025.84 | 0 | 0 | 0 | 1025.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56637 | 132.396 | 69.2996 | 0 | 0 | 5.5739 | 57.6453 | 265.481 | [6 empty] | -- | -- | Successful (86 warnings) | 2.1783 | 113478 | 21268.6 | 0 | 617.903 | 0 | 56504.6 | 191872 | 77659.4 | 0 | 424.5 | 269956 | 375.104 | 0 | 0 | 0 | 0 | 1024.12 | 0 | 1399.23 | 0 | 0 | 0 | 1399.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6455 | 149.582 | 22.6435 | 0 | 0.43485 | 6.0485 | 55.5721 | 236.926 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:01:31 | 0500115-RetlMed-EnvelopeRoofInsulation | 500115 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 2:06 | FAIL | -26.38 | -- | -- | Successful (92 warnings) | 0 | 95660.8 | 73369.9 | 0 | 0 | 0 | 58788 | 227819 | 77659.4 | 0 | 202.152 | 305680 | 74.4204 | 0 | 0 | 0 | 0 | 943.578 | 0 | 1018 | 0 | 0 | 0 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5105 | 130.266 | 69.2988 | 0 | 0 | 5.5739 | 57.6453 | 263.295 | [6 empty] | -- | -- | Successful (86 warnings) | 2.1783 | 113478 | 21268.6 | 0 | 617.903 | 0 | 56504.6 | 191872 | 77659.4 | 0 | 424.5 | 269956 | 375.104 | 0 | 0 | 0 | 0 | 1024.12 | 0 | 1399.23 | 0 | 0 | 0 | 1399.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6455 | 149.582 | 22.6435 | 0 | 0.43485 | 6.0485 | 55.5721 | 236.926 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-23 14:55:15 | 0500215-RetlMed-EnvelopeWallInsulation | 500215 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 2:06 | FAIL | -26.33 | -- | -- | Successful (92 warnings) | 0 | 95886.6 | 73369.9 | 0 | 0 | 0 | 58788 | 228044 | 77659.4 | 0 | 202.152 | 305906 | 67.3085 | 0 | 0 | 0 | 0 | 943.577 | 0 | 1010.89 | 0 | 0 | 0 | 1010.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45978 | 130.269 | 69.2988 | 0 | 0 | 5.5739 | 57.6453 | 263.247 | [6 empty] | -- | -- | Successful (86 warnings) | 2.1783 | 113478 | 21268.6 | 0 | 617.903 | 0 | 56504.6 | 191872 | 77659.4 | 0 | 424.5 | 269956 | 375.104 | 0 | 0 | 0 | 0 | 1024.12 | 0 | 1399.23 | 0 | 0 | 0 | 1399.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6455 | 149.582 | 22.6435 | 0 | 0.43485 | 6.0485 | 55.5721 | 236.926 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160923_2016_SST_DG\
| 2016-Sep-22 23:05:51 | 0500315-RetlMed-EnvelopeHeavy | 500315 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 2:06 | FAIL | -27.08 | -- | -- | Successful (92 warnings) | 0 | 96273.9 | 73369.9 | 0 | 0 | 0 | 58788 | 228432 | 77659.4 | 0 | 202.152 | 306293 | 67.2883 | 0 | 0 | 0 | 0 | 943.572 | 0 | 1010.86 | 0 | 0 | 0 | 1010.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46197 | 131.018 | 69.2988 | 0 | 0 | 5.5739 | 57.6453 | 263.998 | [6 empty] | -- | -- | Successful (86 warnings) | 2.1783 | 113478 | 21268.6 | 0 | 617.903 | 0 | 56504.6 | 191872 | 77659.4 | 0 | 424.5 | 269956 | 375.104 | 0 | 0 | 0 | 0 | 1024.12 | 0 | 1399.23 | 0 | 0 | 0 | 1399.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6455 | 149.582 | 22.6435 | 0 | 0.43485 | 6.0485 | 55.5721 | 236.926 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:07:40 | 0500706-RetlMed-EnvelopeRoofInsulation | 500706 | TORRANCE_722955 | Title24Compliance | 1:44 | FAIL | -33.92 | -- | -- | Successful (90 warnings) | 0 | 24757.2 | 70571.5 | 0 | 0 | 0 | 56247.6 | 151576 | 77659.4 | 0 | 200.149 | 229436 | 123.949 | 0 | 0 | 0 | 0 | 1089.28 | 0 | 1213.23 | 0 | 0 | 0 | 1213.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84512 | 47.0076 | 67.0059 | 0 | 0 | 6.3883 | 54.5895 | 175.836 | [6 empty] | -- | -- | Successful (80 warnings) | 4.0616 | 40595.1 | 16022.7 | 0 | 1179.99 | 0 | 53875.9 | 111678 | 77659.4 | 0 | 424.5 | 189762 | 704.785 | 0 | 0 | 0 | 0 | 1178.96 | 0 | 1883.74 | 0 | 0 | 0 | 1883.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8278 | 61.2176 | 15.998 | 0 | 0.82784 | 6.914 | 52.1423 | 141.928 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:09:29 | 0500806-RetlMed-EnvelopeWallInsulation | 500806 | TORRANCE_722955 | Title24Compliance | 1:44 | FAIL | -34.41 | -- | -- | Successful (90 warnings) | 0 | 25289.8 | 70571.5 | 0 | 0 | 0 | 56247.6 | 152109 | 77659.4 | 0 | 200.149 | 229969 | 110.519 | 0 | 0 | 0 | 0 | 1089.28 | 0 | 1199.8 | 0 | 0 | 0 | 1199.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75213 | 47.5954 | 67.0059 | 0 | 0 | 6.3884 | 54.5895 | 176.331 | [6 empty] | -- | -- | Successful (80 warnings) | 4.0616 | 40595.1 | 16022.7 | 0 | 1179.99 | 0 | 53875.9 | 111678 | 77659.4 | 0 | 424.5 | 189762 | 704.785 | 0 | 0 | 0 | 0 | 1178.96 | 0 | 1883.74 | 0 | 0 | 0 | 1883.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8278 | 61.2176 | 15.998 | 0 | 0.82784 | 6.914 | 52.1423 | 141.928 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:11:20 | 0500906-RetlMed-EnvelopeHeavy | 500906 | TORRANCE_722955 | Title24Compliance | 1:47 | FAIL | -32.66 | -- | -- | Successful (86 warnings) | 0 | 24064.2 | 70571.5 | 0 | 0 | 0 | 56247.6 | 150883 | 77659.4 | 0 | 200.149 | 228743 | 108.381 | 0 | 0 | 0 | 0 | 1089.27 | 0 | 1197.65 | 0 | 0 | 0 | 1197.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73925 | 45.8578 | 67.0059 | 0 | 0 | 6.3883 | 54.5895 | 174.581 | [6 empty] | -- | -- | Successful (80 warnings) | 4.0616 | 40595.1 | 16022.7 | 0 | 1179.99 | 0 | 53875.9 | 111678 | 77659.4 | 0 | 424.5 | 189762 | 704.785 | 0 | 0 | 0 | 0 | 1178.96 | 0 | 1883.74 | 0 | 0 | 0 | 1883.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8278 | 61.2176 | 15.998 | 0 | 0.82784 | 6.914 | 52.1423 | 141.928 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:13:08 | 0506007-RetlMed-Daylighting SRRBaseHighVT | 506007 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 1:44 | FAIL | -32.19 | -- | -- | Successful (90 warnings) | 0 | 16685 | 70571.5 | 0 | 0 | 0 | 55234.1 | 142491 | 77659.4 | 0 | 201.456 | 220351 | 61.5675 | 0 | 0 | 0 | 0 | 1072.59 | 0 | 1134.15 | 0 | 0 | 0 | 1134.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41941 | 38.8024 | 68.0278 | 0 | 0 | 6.3358 | 55.4279 | 169.013 | [6 empty] | -- | -- | Successful (81 warnings) | 2.2438 | 34019 | 15831.4 | 0 | 876.154 | 0 | 55436.3 | 106165 | 77659.4 | 0 | 424.5 | 184249 | 397.115 | 0 | 0 | 0 | 0 | 1161.21 | 0 | 1558.32 | 0 | 0 | 0 | 1558.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7547 | 54.5928 | 16.0599 | 0 | 0.62895 | 6.8592 | 55.9374 | 136.833 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-23 14:57:04 | 0506107-RetlMed-Daylighting SRR4.67 | 506107 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 1:44 | FAIL | -34.41 | -- | -- | Successful (90 warnings) | 0 | 18404.6 | 70571.5 | 0 | 0 | 0 | 50085 | 139061 | 77659.4 | 0 | 201.456 | 216922 | 71.1351 | 0 | 0 | 0 | 0 | 1072.59 | 0 | 1143.72 | 0 | 0 | 0 | 1143.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48659 | 41.3115 | 68.0278 | 0 | 0 | 6.3358 | 50.2525 | 166.414 | [6 empty] | -- | -- | Successful (82 warnings) | 2.6628 | 35458.3 | 16128.3 | 0 | 937.647 | 0 | 47830.8 | 100358 | 77659.4 | 0 | 424.5 | 178442 | 468.172 | 0 | 0 | 0 | 0 | 1161.21 | 0 | 1629.38 | 0 | 0 | 0 | 1629.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2664 | 56.7457 | 16.4362 | 0 | 0.67377 | 6.8592 | 48.0189 | 132 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160923_2016_SST_DG\
| 2016-Sep-22 23:16:42 | 0506207-RetlMed-Daylighting SRR4.67HighVT | 506207 | SAN-DIEGO-LINDBERGH_722900 | Title24Compliance | 1:42 | FAIL | -34.12 | -- | -- | Successful (90 warnings) | 0 | 18108.9 | 70571.5 | 0 | 0 | 0 | 50085 | 138765 | 77659.4 | 0 | 201.456 | 216626 | 72.8328 | 0 | 0 | 0 | 0 | 1072.59 | 0 | 1145.42 | 0 | 0 | 0 | 1145.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4982 | 41.0119 | 68.0278 | 0 | 0 | 6.3358 | 50.2525 | 166.126 | [6 empty] | -- | -- | Successful (82 warnings) | 2.6628 | 35458.3 | 16128.3 | 0 | 937.647 | 0 | 47830.8 | 100358 | 77659.4 | 0 | 424.5 | 178442 | 468.172 | 0 | 0 | 0 | 0 | 1161.21 | 0 | 1629.38 | 0 | 0 | 0 | 1629.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2664 | 56.7457 | 16.4362 | 0 | 0.67377 | 6.8592 | 48.0189 | 132 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:19:23 | 0512815-RetlMed-SZVAV | 512815 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 2:37 | PASS | 0.97 | -- | -- | Successful (117 warnings) | 0 | 98315.5 | 36578.8 | 0 | 0 | 0 | 58788 | 193682 | 77659.4 | 0 | 202.152 | 271544 | 129.931 | 0 | 0 | 0 | 0 | 943.579 | 0 | 1073.51 | 0 | 0 | 0 | 1073.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91128 | 132.961 | 38.8601 | 0 | 0 | 5.5739 | 57.6453 | 235.952 | [6 empty] | -- | -- | Successful (86 warnings) | 2.1783 | 113478 | 21268.6 | 0 | 617.903 | 0 | 56504.6 | 191872 | 77659.4 | 0 | 424.5 | 269956 | 375.104 | 0 | 0 | 0 | 0 | 1024.12 | 0 | 1399.23 | 0 | 0 | 0 | 1399.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6455 | 149.582 | 22.6435 | 0 | 0.43485 | 6.0485 | 55.5721 | 236.926 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-22 23:21:20 | 0513006-RetlMed-SZVAV | 513006 | TORRANCE_722955 | Title24Compliance | 1:52 | PASS | 12.3 | -- | -- | Successful (117 warnings) | 0 | 31602.1 | 13744.6 | 0 | 0 | 0 | 56247.6 | 101594 | 77659.4 | 0 | 200.149 | 179454 | 280.988 | 0 | 0 | 0 | 0 | 1089.28 | 0 | 1370.27 | 0 | 0 | 0 | 1370.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9305 | 53.6563 | 13.0557 | 0 | 0 | 6.3883 | 54.5895 | 129.62 | [6 empty] | -- | -- | Successful (80 warnings) | 4.0616 | 40595.1 | 16022.7 | 0 | 1179.99 | 0 | 53875.9 | 111678 | 77659.4 | 0 | 424.5 | 189762 | 704.785 | 0 | 0 | 0 | 0 | 1178.96 | 0 | 1883.74 | 0 | 0 | 0 | 1883.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8278 | 61.2176 | 15.998 | 0 | 0.82784 | 6.914 | 52.1423 | 141.928 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4377) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Data\EPW\ | C:\Users\nikhilk\Documents\CBECC-Com 2016-2-1 Projects\0500\BatchOut_160922_2016_SST_DG\
| 2016-Sep-19 09:26:35 | 1000006-RetlStrp-BaselinePSZ | 1000006 | TORRANCE_722955 | Title24Compliance | 1:06 | FAIL | -37.13 | -- | -- | Successful (116 warnings) | 0 | 27445.6 | 64644.1 | 0 | 0 | 0 | 65661.9 | 157752 | 81817.9 | 0 | 0 | 239570 | 118.08 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1406.24 | 0 | 0 | 0 | 1406.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87088 | 53.9441 | 67.0059 | 0 | 0 | 8.2474 | 71.0774 | 201.146 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:27:43 | 1000006-RetlStrp-BaselinePTAC | 1000006 | TORRANCE_722955 | Title24Compliance | 1:03 | FAIL | -9.56 | -- | -- | Successful (108 warnings) | 3250.23 | 26760.8 | 37009.5 | 0 | 0 | 0 | 65661.9 | 132683 | 81817.9 | 0 | 0 | 214500 | 0 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1288.16 | 0 | 0 | 0 | 1288.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4741 | 53.3853 | 38.3907 | 0 | 0 | 8.2474 | 71.0774 | 173.575 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:28:49 | 1000015-RetlStrp-BaselinePSZ | 1000015 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:01 | PASS | 2.83 | -- | -- | Successful (116 warnings) | 0 | 102479 | 84037.3 | 0 | 0 | 0 | 66585.6 | 253102 | 81817.9 | 0 | 0 | 334919 | 63.0895 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1179.87 | 0 | 0 | 0 | 1179.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46655 | 150.847 | 86.6525 | 0 | 0 | 7.2015 | 72.6705 | 317.838 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:29:52 | 1000015-RetlStrp-BaselinePTAC | 1000015 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 0:59 | PASS | 44.65 | -- | -- | Successful (108 warnings) | 1857.13 | 97212.5 | 47985.4 | 0 | 0 | 0 | 66585.6 | 213641 | 81817.9 | 0 | 0 | 295459 | 0 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1116.78 | 0 | 0 | 0 | 1116.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4074 | 145.295 | 49.4458 | 0 | 0 | 7.2015 | 72.6705 | 276.02 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:30:58 | 1009215-RetlStrp-HVACPSZ DXCOP | 1009215 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:01 | PASS | 27.18 | -- | -- | Successful (116 warnings) | 0 | 85937.4 | 84037.3 | 0 | 0 | 0 | 66585.6 | 236560 | 81817.9 | 0 | 0 | 318378 | 63.0895 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1179.87 | 0 | 0 | 0 | 1179.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46655 | 126.499 | 86.6525 | 0 | 0 | 7.2015 | 72.6705 | 293.49 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:32:04 | 1009315-RetlStrp-HVACPSZ HeatEff | 1009315 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:01 | PASS | 2.87 | -- | -- | Successful (116 warnings) | 0 | 102479 | 84037.3 | 0 | 0 | 0 | 66585.6 | 253102 | 81817.9 | 0 | 0 | 334919 | 57.4816 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1174.26 | 0 | 0 | 0 | 1174.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42508 | 150.847 | 86.6525 | 0 | 0 | 7.2015 | 72.6705 | 317.797 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:33:09 | 1009415-RetlStrp-HVACPSZ EconomizerControl | 1009415 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:01 | FAIL | -6.48 | -- | -- | Successful (116 warnings) | 0 | 114875 | 84037.3 | 0 | 0 | 0 | 66585.6 | 265498 | 81817.9 | 0 | 0 | 347316 | 57.1228 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1173.9 | 0 | 0 | 0 | 1173.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41909 | 160.208 | 86.6525 | 0 | 0 | 7.2015 | 72.6705 | 327.152 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:34:21 | 1009806-RetlStrp-HVACPSZ DXCOP | 1009806 | TORRANCE_722955 | Title24Compliance | 1:08 | FAIL | -21.78 | -- | -- | Successful (116 warnings) | 0 | 18604.5 | 64644.1 | 0 | 0 | 0 | 65661.9 | 148910 | 81817.9 | 0 | 0 | 230728 | 118.08 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1406.24 | 0 | 0 | 0 | 1406.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87088 | 38.5856 | 67.0059 | 0 | 0 | 8.2474 | 71.0774 | 185.787 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:35:32 | 1009906-RetlStrp-HVACPSZ HeatEff | 1009906 | TORRANCE_722955 | Title24Compliance | 1:06 | FAIL | -37.05 | -- | -- | Successful (116 warnings) | 0 | 27445.6 | 64644.1 | 0 | 0 | 0 | 65661.9 | 157752 | 81817.9 | 0 | 0 | 239570 | 107.584 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1395.75 | 0 | 0 | 0 | 1395.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79347 | 53.9441 | 67.0059 | 0 | 0 | 8.2474 | 71.0774 | 201.068 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:36:44 | 1010006-RetlStrp-HVACPSZ EconomizerControl | 1010006 | TORRANCE_722955 | Title24Compliance | 1:07 | FAIL | -56.54 | -- | -- | Successful (116 warnings) | 0 | 51798.9 | 64644.1 | 0 | 0 | 0 | 65661.9 | 182105 | 81817.9 | 0 | 0 | 263923 | 102.324 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1390.49 | 0 | 0 | 0 | 1390.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75025 | 73.4682 | 67.0059 | 0 | 0 | 8.2474 | 71.0774 | 220.549 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:37:48 | 1010115-RetlStrp-HVACPTAC DXCOP | 1010115 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:00 | PASS | 68.1 | -- | -- | Successful (108 warnings) | 1857.13 | 81521.3 | 47985.4 | 0 | 0 | 0 | 66585.6 | 197949 | 81817.9 | 0 | 0 | 279767 | 0 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1116.78 | 0 | 0 | 0 | 1116.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4074 | 121.843 | 49.4458 | 0 | 0 | 7.2015 | 72.6705 | 252.568 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:38:56 | 1010306-RetlStrp-HVACPTAC DXCOP | 1010306 | TORRANCE_722955 | Title24Compliance | 1:03 | FAIL | -0.94 | -- | -- | Successful (108 warnings) | 3250.23 | 22441.3 | 37009.5 | 0 | 0 | 0 | 65661.9 | 128363 | 81817.9 | 0 | 0 | 210181 | 0 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1288.16 | 0 | 0 | 0 | 1288.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4741 | 44.7683 | 38.3907 | 0 | 0 | 8.2474 | 71.0774 | 164.958 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:40:49 | 1010515-RetlStrp-FPFC | 1010515 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:47 | PASS | 69.28 | -- | -- | Successful (137 warnings) | 0.43715 | 67141.9 | 60240.4 | 805.577 | 21918 | 0 | 66585.6 | 216692 | 81817.9 | 0 | 0 | 298510 | 83.311 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1200.09 | 0 | 0 | 0 | 1200.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61547 | 83.0652 | 61.8862 | 1.6255 | 24.3069 | 7.2015 | 72.6705 | 251.371 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:42:21 | 1010606-RetlStrp-FPFC | 1010606 | TORRANCE_722955 | Title24Compliance | 1:28 | FAIL | -6.93 | -- | -- | Successful (106 warnings) | 0.85773 | 22113.8 | 37876.3 | 70.0071 | 10724.2 | 0 | 65661.9 | 136447 | 81817.9 | 0 | 0 | 218265 | 163.466 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1451.63 | 0 | 0 | 0 | 1451.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2086 | 37.2151 | 39.3822 | 0.25646 | 13.5475 | 8.2474 | 71.0774 | 170.935 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:43:27 | 1013715-RetlStrp-EvapCooler | 1013715 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:01 | PASS | 41.48 | -- | -- | Successful (118 warnings) | 0 | 64909.7 | 84037.3 | 0 | 0 | 0 | 66585.6 | 215533 | 81817.9 | 0 | 0 | 297351 | 61.4341 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1178.21 | 0 | 0 | 0 | 1178.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45756 | 112.214 | 86.6525 | 0 | 0 | 7.2015 | 72.6705 | 279.196 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:44:38 | 1013906-RetlStrp-EvapCooler | 1013906 | TORRANCE_722955 | Title24Compliance | 1:06 | FAIL | -13.93 | -- | -- | Successful (116 warnings) | 0 | 11961.1 | 64644.1 | 0 | 0 | 0 | 65661.9 | 142267 | 81817.9 | 0 | 0 | 224085 | 118.083 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1406.25 | 0 | 0 | 0 | 1406.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8709 | 30.7365 | 67.0059 | 0 | 0 | 8.2474 | 71.0774 | 177.938 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:45:43 | 1014315-RetlStrp-WSHP | 1014315 | PALM-SPRINGS-INTL_722868 | Title24Compliance | 1:01 | PASS | 56.07 | -- | -- | Successful (118 warnings) | 159.351 | 93676.2 | 37008.5 | 0.42008 | 5260.49 | 0 | 66585.6 | 202691 | 81817.9 | 0 | 0 | 284509 | 95.082 | 0 | 0 | 0 | 0 | 1116.78 | 0 | 1211.86 | 0 | 0 | 0 | 1211.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83778 | 139.467 | 38.2299 | 0.00030705 | 6.1938 | 7.2015 | 72.6705 | 264.6 | [6 empty] | -- | -- | Successful (2 severe errors, 110 warnings) | 5.9507 | 128939 | 48073.7 | 0 | 673.751 | 0 | 66585.6 | 244278 | 81817.9 | 0 | 0 | 326096 | 1025.71 | 0 | 0 | 0 | 0 | 1101.51 | 0 | 2127.22 | 0 | 0 | 0 | 2127.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.427 | 177.293 | 56.6271 | 0 | 0.54626 | 7.1023 | 72.6705 | 320.666 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\
| 2016-Sep-19 09:46:52 | 1014506-RetlStrp-WSHP | 1014506 | TORRANCE_722955 | Title24Compliance | 1:04 | FAIL | -12.68 | -- | -- | Successful (106 warnings) | 359.478 | 26809.3 | 36790.9 | 0 | 3399.54 | 0 | 65661.9 | 133021 | 81817.9 | 0 | 0 | 214839 | 142.025 | 0 | 0 | 0 | 0 | 1288.16 | 0 | 1430.19 | 0 | 0 | 0 | 1430.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3244 | 53.6835 | 38.1314 | 0 | 4.2361 | 8.2474 | 71.0774 | 176.7 | [6 empty] | -- | -- | Successful (113 warnings) | 3.0751 | 37790.3 | 15428.4 | 0 | 476.15 | 0 | 65661.9 | 119360 | 81817.9 | 0 | 0 | 201178 | 535.76 | 0 | 0 | 0 | 0 | 1268.61 | 0 | 1804.37 | 0 | 0 | 0 | 1804.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9972 | 61.8429 | 18.6159 | 0 | 0.3649 | 8.122 | 71.0774 | 164.02 | [6 empty] | CBECC-Com 2016.2.1 (868) | BEMCmpMgr 2016.2.1 (4372) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.1.d869ebc332 | 8.5 | - | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Data\EPW\ | C:\Users\nikhilk\Documents\svn-CBECC-Com\CBECC-Com13\Projects\SoftwareSensitivity2016 Tests\DetailedGeometry\BO_0918_STDG16\

## Sheet3 (hidden)
Small Office Building (02000CZ-OffSml) | Medium Office Building ((0300CZ-OffMed)) | Large Office Building (0400CZ-OffLrg) | Stand-alone Retail (0500CZ-RetlMed) | Strip Mall-PSZ System (1000CZ-RetlStrp)
5500 | 53600 | 498600 | 24695 | 22500
(90.8 ft x 60.5ft) | (163.8 ft x 109.2 ft) | (240 ft x 160 ft) | (178 ft x 139 ft) | (300 ft x 75 ft)