## Rev1 Based on ACH (hidden)
Input Value
Calculated Value
| Sash Control Fraction | 1 |  |  |  | VAV Exhaust | 0.12
| Zone SF | 900 | ft2 |  |  | CAV Exhaust | 0.9
| Zone Height | 9 | ft
| Zone Volume | 8100 | ft3 |  |  | Fraction of Vent | Fraction of Exh
| Code Min Occupied (Design) Exhaust Flow (CFM_eu) | 900 | cfm | 1 | cfm/ft2 | 0.55556
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 1620 | cfm | 12 | ACH | 1 | 1
| Unoccupied (Min) Exhaust Flow (CFM_eu) | 194.4 | cfm | 1.44 | ACH | 0.12 | 0.12
| Unoccupied (Min) Exhaust Flow, CAV (CFM_eu) | 1458 |  | 10.8 | ACH | 0.9 | 0.9
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 1620 | cfm | 12 | ACH | 1 | 1
| Unoccupied (Min) Terminal Flow (CFM_tu) | 270 | cfm | 2 | ACH | 0.16667 | 0.16667
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 0 | cfm | 0 | ACH | 0 | 0
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 0 | cfm | 2 | ACH | 0 | 0
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustHoodVAVNoSashCtrl | Fraction | WD | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.4128 | 0.4718 | 0.37 | 0.37 | 0.4128 | 0.5308 | 0.4718 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sat | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sun | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
| LabExhaustHoodVAVSashCtrl | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| LabExhaustHoodCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
2) | Multiply CFM_eu x 1)
| Exhaust Flow | 12 | WD | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 3.6744 | 4.5684 | 5.0148 | 3.228 | 3.6744 | 4.5684 | 5.4624 | 5.0148 | 3.6744 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
|  |  | Sat | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
|  |  | Sun | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
|  |  | WD | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sat | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sun | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
3) | Subtract CFM_vumin from 2)
| Diff Vent vs Exh |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6744 | 2.5684 | 3.0148 | 1.228 | 1.6744 | 2.5684 | 3.4624 | 3.0148 | 1.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WD | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
|  |  | Sat | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
|  |  | Sun | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
4) | Add 'AllOn' schedule x CFM_vumin to 3)
| TerminalUnit (Vent) Flow | 2 | WD | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3.6744 | 4.5684 | 5.0148 | 3.228 | 3.6744 | 4.5684 | 5.4624 | 5.0148 | 3.6744 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Sat | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Sun | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | WD | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sat | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sun | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
5) | Multiply 1/CFM_eu x 4)
| TerminalUnit (Vent) Flow Fraction | 0.083333 | WD | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  |  | Sat | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  |  | Sun | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  | 0.092593 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E16: David Reddy: IN simulation, can't be less than min exhaust
Note on E17: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## Proposed
Input Value
Calculated Value
| Exhaust Control | VAV
| Zone SF | 5502 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 10 | ft |  |  |  | VAV Auto Sash Min Frac | 0.35431
| Zone Volume | 55020 | ft3
| Total Fume Hood Length | 57
| Hood Density | 10.3599
| Vertical Sash Fume Hood Exhaust Flow | 14250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 0.5
| Other Exhaust Flow | 422
| Zone Exh Flow Auto Sash Control Frac | 0.48562
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 5198.5 | cfm | 5.669 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 3668 | cfm | 4 | ACH | 0.25 | 0.088579
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 3668 | cfm | 4 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.25
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 3668 | cfm | 4 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.36917 | 0.44831 | 0.44831 | 0.39888 | 0.39888 | 0.44831 | 0.44831 | 0.44831 | 0.44831 | 0.44831 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431
|  |  | Sat | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.35917 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431
|  |  | Sun | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.35917 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.36917 | 0.44831 | 0.44831 | 0.39888 | 0.39888 | 0.44831 | 0.44831 | 0.44831 | 0.44831 | 0.44831 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431
|  |  | Sat | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.35917 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431
|  |  | Sun | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.35917 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.35431 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048562 | 0.014856 | 0.093993 | 0.093993 | 0.044569 | 0.044569 | 0.093993 | 0.093993 | 0.093993 | 0.093993 | 0.093993 | 0.029712 | 0.0048562 | 0.0048562 | 0.0048562 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048562 | 0.0048562 | 0.029712 | 0.029712 | 0.029712 | 0.029712 | 0.0048562 | 0.0048562 | 0.0048562 | 0.0048562 | 0.0048562 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048562 | 0.0048562 | 0.029712 | 0.029712 | 0.029712 | 0.029712 | 0.0048562 | 0.0048562 | 0.0048562 | 0.0048562 | 0.0048562 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.35431 | WD | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.36917 | 0.44831 | 0.44831 | 0.39888 | 0.39888 | 0.44831 | 0.44831 | 0.44831 | 0.44831 | 0.44831 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431
|  |  | Sat | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.35917 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431
|  |  | Sun | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35917 | 0.35917 | 0.38403 | 0.38403 | 0.38403 | 0.38403 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35917 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431 | 0.35431
Calculated flows for graph
| VAV Exhaust |  | WD | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.7467 | 5.9067 | 7.1729 | 7.1729 | 6.3821 | 6.3821 | 7.1729 | 7.1729 | 7.1729 | 7.1729 | 7.1729 | 6.1444 | 5.7467 | 5.7467 | 5.7467 | 5.669 | 5.669
|  |  | Sat | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.7467 | 5.7467 | 6.1444 | 6.1444 | 6.1444 | 6.1444 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669
|  |  | Sun | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.7467 | 5.7467 | 6.1444 | 6.1444 | 6.1444 | 6.1444 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669
| TerminalUnit (Vent) Flow Fraction |  | WD | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.7467 | 5.9067 | 7.1729 | 7.1729 | 6.3821 | 6.3821 | 7.1729 | 7.1729 | 7.1729 | 7.1729 | 7.1729 | 6.1444 | 5.7467 | 5.7467 | 5.7467 | 5.669 | 5.669
|  |  | Sat | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.7467 | 5.7467 | 6.1444 | 6.1444 | 6.1444 | 6.1444 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669
|  |  | Sun | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.7467 | 5.7467 | 6.1444 | 6.1444 | 6.1444 | 6.1444 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.7467 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669 | 5.669
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## Baseline
Input Value
Calculated Value
| Exhaust Control | VAV
| Zone SF | 5502 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 10 | ft |  |  |  | VAV Auto Sash Min Frac | 0.20863
| Zone Volume | 55020 | ft3
| Total Fume Hood Length | 57
| Hood Density | 10.3599
| Vertical Sash Fume Hood Exhaust Flow | 14250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 1
| Other Exhaust Flow | 422
| Zone Exh Flow Auto Sash Control Frac | 0.97124
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 3061 | cfm | 3.3381 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 3668 | cfm | 4 | ACH | 0.25 | 0.052157
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 3668 | cfm | 4 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.25
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 3668 | cfm | 4 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.22834 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863
|  |  | Sat | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
|  |  | Sun | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.22834 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863
|  |  | Sat | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
|  |  | Sun | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.25 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086615 | 0.086615 | 0.017766 | 0.017766 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.25 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Calculated flows for graph
| VAV Exhaust |  | WD | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.6535 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381
|  |  | Sat | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.4935 | 3.9689 | 3.9689 | 3.9689 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381
|  |  | Sun | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.4935 | 3.9689 | 3.9689 | 3.9689 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381
| TerminalUnit (Vent) Flow Fraction |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## Baseline_old (hidden)
Input Value
Calculated Value
| Sash Control Fraction | 1 |  |  |  | VAV Exhaust | 0.12
| Zone SF | 5502 | ft2 |  |  | CAV Exhaust | 0.9
| Zone Height | 10 | ft
| Zone Volume | 55020 | ft3
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 5502 | cfm | 6 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 660.24 | cfm | 0.72 | ACH
| Unoccupied (Min) Exhaust Flow, CAV (CFM_caveu) | 4951.8 | cfm | 5.4 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 5502 | cfm | 6 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 2751 | cfm | 3 | ACH | 0.5 | 0.06
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 2751 | cfm | 3 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.5
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 2751 | cfm | 3 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustHoodVAVNoSashCtrl | Fraction | WD | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.4128 | 0.4718 | 0.37 | 0.37 | 0.4128 | 0.5308 | 0.4718 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sat | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sun | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
| LabExhaustHoodVAVSashCtrl | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| LabExhaustHoodCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| CAV Exhaust |  | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.5 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAV Exhaust |  | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.5 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Calculated flows for graph
| VAV Exhaust |  | WD | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 1.8372 | 2.2842 | 2.5074 | 1.614 | 1.8372 | 2.2842 | 2.7312 | 2.5074 | 1.8372 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
|  |  | Sat | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
|  |  | Sun | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
| TerminalUnit (Vent) Flow Fraction |  | WD | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  | Sat | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  | Sun | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| CAV Exhaust |  | WD | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sat | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sun | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
| TerminalUnit (Vent) Flow Fraction |  | WD | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sat | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sun | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E15: David Reddy: IN simulation, can't be less than min exhaust
Note on E16: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.