## Prototype Model
Prototype Name | II | III | IV
Prototype Description | Medium Office Building (0300CZ-OffMed) | Large Office Building (0400CZ-OffLrg) | Retail Medium (0500CZ-RetlMed)
Vintage | New Construction | New Construction | New Construction
Location | CZ-6/16 | CZ-7/6/16 | CZ-6/7/15
Fuel Type | gas, electricity | gas, electricity | gas, electricity
Total Floor Area (sq feet) | 53600 (163.8 ft x 109.2 ft) | 498,600 (240 ft x 160 ft) | 24695 (178 ft x 139 ft)
Building shape
Aspect Ratio | 1.5 | 1.5 | 1.28
Number of Floors | 3 | 13 (Including basement) | 1
Window Fraction (Window-to-Wall Ratio) | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) | 7.1% (Window Dimensions: 82.136 ft x 5 ft, 9.843 ft x 8.563 ft and 82.136 ft x 5 on the street facing facade)
Window Locations | evenly distributed along four façades | evenly distributed along four façades | Windows only on the street facing façade (25.4% WWR)
Shading Geometry | none | none | none
Azimuth | non-directional | non-directional | non-directional
Thermal Zoning | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 40%, Core 60% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 33%, Core 67% | Five thermal zones Refer StandAloneRetailArea for details
Floor to floor height (feet) | 13 | 13, Basement - 8 | 20
Floor to ceiling height (feet) | 9 (4 ft above-ceiling plenum) | 9 | 20 (Core retail, Front Entry) 15 (Point of Sale, Front Retail, Back Space)
Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | 3 ft | 3.74 ft (top of the window is 8.73 ft high with 5 ft high glass)
Exterior walls
Construction | Metal Framed Wall | Metal Framed Wall | Metal Framed Wall
Construction Assembly Layers | Refer MetalFrameWall / Metal Framed Wall | Refer MetalFrameWall / Metal Framed Wall | Refer MetalFrameWall / Metal Framed Wall
Refer BasementWall
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | 0.062 | Exterior Wall U: 0.062 | 0.062
Dimensions | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio
Tilts and orientations | Vertical | Vertical | Vertical
Roof
Construction | Roof | Roof | Roof
Construction Assembly Layers | Refer Roof | Refer Roof | Refer Roof
U-factor (Btu / h * ft2 * °F) | 0.034 | 0.034 | 0.034
Aged Solar Reflectance Aged Thermal Emittance | 0.08 0.75 | 0.08 0.75 | 0.08 0.75
Tilts and orientations | Horizontal | Horizontal | Horizontal
Window
Glass-Type and frame | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) | 0.36 | 0.36 | 0.36
SHGC | 0.25 | 0.25 | 0.25
Visible transmittance | 0.42 | 0.42 | 0.42
Operable area | 0 | 0 | 0
Skylight | NA | NA
Dimensions |  |  | Skylight to Roof Ratio- 2.07 % Core Retail, Refer Skylight Layout for details
Glass-Type and frame |  |  | Glass, curb mounted skylight with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) |  |  | 0.58
SHGC |  |  | 0.25
Visible transmittance |  |  | 0.49
Foundation
Foundation Type | Slab Floor F-factor method | Slab Floor F-factor method | Slab Floor F-factor method
Construction | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation
F factor (Btu / h * ft2 * °F) | 0.72 | 0.72 | F factor= 0.72
Thermal properties for basement walls | NA | Refer BasementWall for detailed description | NA
Interior Surfaces
Construction | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling
Construction Assembly Layers | Interior wall Interior Floor Drop Ceiling | Interior wall Interior Floor Drop Ceiling | Interior wall
Internal Mass | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
Infiltration | 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) | 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) | 0.0448 cfm/sf of above grade exterior wall surface area
HVAC System Type
System Type | Packaged VAV with hot-water reheat with one system per floor serving all zones in the floor | VAV with hot-water reheat with one system per floor serving all zones in the floor | Indirectly Conditioned Front_entry, Packaged single zone air conditioning unit for other zones.
Heating type | Gas condensing boiler | Gas condensing boiler | Unconditioned for front_entry. Gas furnace inside the packaged air conditioning unit for all others.
Cooling type | Direct Expansion | Water cooled Centrifugal chillers (2) | No cooling for front_entry. Packaged air conditioning unit for all others
Distribution and terminal units | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 20% of the zone maximum air flow rate. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 20% of the zone maximum air flow rate. | Constant air volume air distribution 4 single-zone roof top units serving thermal zones back_space, point_of_sale, core_retail, and front_retail.
HVAC Sizing
Cooling | Refer Sizing Values | Refer Sizing Values | Refer Sizing Values
Heating | Refer Sizing Values | Refer Sizing Values | Refer Sizing Values
HVAC Efficiency
Cooling | EER-11.00, IEER-12.4 (Bottom VAV, Mid and Top VAV). Note: EER, COP includes fan heat | 0.585 kw/ton, 0.380 IPLV | EER-11.20, IEER- 12.9 (BackSpace/Core Retail) EER-11.20 SEER-13.0 (Point of Sale) EER-11.20 SEER-13.6 (Front Retail) Indirect Heating and Cooling for front_entry) Note: EER, COP includes fan heat
Heating | 80% | 80% | 82%
HVAC Control
Thermostat Setpoint | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating
Thermostat Setback | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating
Design Supply air temperature | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F
Supply air temperature reset | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | No SAT Control
Zone control | DDC at zone level and Dual Max Reheat control | DDC at zone level and Dual Max Reheat control | CO2 sensor
Chilled water supply temperatures | NA | 44°F | NA
Chilled water return temperatures | NA | 64°F | NA
Chilled water supply temperature reset | NA | Fixed | NA
Condenser Type | NA | Water-cooled, no reset | NA
Hot water supply temperatures | 180°F | 180°F | NA
Hot water supply temperature reset | Fixed | Fixed | NA
Economizers | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated), 80F high DB lockout
Ventilation | Max of 15 cfm/person, 0.15 cfm/ft2, | Max of 15 cfm/person, 0.15 cfm/ft2, | Back Space - Max of 15 cfm/person or 0.15 cfm/ft2 Point of Sale & Core and Front Retail -Max of 15 cfm/person or 0.20 cfm/ft2
Supply Fan
Fan type | Variable Volume | Constant volume for Basement, Variable Volume for all others | Constant Volume for all Conditioned zones
Supply Fan Total Efficiency (%) | 65% | 65% (for all VAV fans) | 60% (all fans)
Fan Motor Efficiency | 95% | 95% | 90% (all fans)
Supply Fan Pressure Rise | 4 inch H2O | 4 inH2O | 2.5in H2O (all fans)
Pump
Pump Type | HW: Constant Speed | HW: Constant Speed variable flow, Cooling Tower:Constant Speed, CHW: Variable Primary | NA
Rated Pump Head | HW: 50 ft H20 | HW: 40 ft H20 Cooling Tower: 40 ft H20 Chiller Pumps: 60 ft H20 | NA
Pump Motor Power per Unit Flow | HW: 19 W/gpm | HW: 15 W/gpm, CW: 17.4 W/gpm, ChW Primary: 17.5 W/gpm | NA
Pump Efficiency | Motor efficiency- HW: 0.9 | 0.9 | NA
Cooling Tower
Cooling Tower Type | NA | open cooling tower with variable speed fan | NA
Tower range | NA | 10F delta T | NA
Service Water Heating
SWH type | Storage Tank | Storage Tank | Tank
Fuel type | Natural Gas | Natural Gas | Natural Gas
Efficiency | EF: 0.637, Recovery Eff: 0.780 | TE: 80% | EF: 0.637, Recovery Eff: 0.780
Water temperature setpoint | 135°F | 135 °F | 135°F
Water Heater Max Capacity (Btuh) | 24,949 Btuh | 231,958 Btuh | 32,328 Btuh
Lighting Load
Lighting power density (W/ft2) | 0.75 W/ft2 | 0.75 W/ft2 | Point of sale, Retail-1.2 W/ft2,, Lobby-0.95 W/ft2, Backspace-0.6 W/ft2
Daylighting Controls | Continuous dimming in Primary Daylit areas in Perimeter zones | Continuous dimming in Primary and Secondary Daylit zone in Perimeter zones | Continuous Dimming in Skylit area in Core Retail and in Primary Daylit in Front Entry, Front Retail, Point of Sale
Plug load
Electric power density (W/ft2) | 1.5 W/ft2 | 1.5 W/ft2 | Point of sale, Retail-1.0 W/ft2, Backspace-0.2 W/ft2, Front entry: 0.5 W/ft2
Occupancy
Average people | 10 person / 1000 ft2 x 0.5 Note: 0.5 is the Occupancy Fraction | 10 person / 1000 ft2 x 0.5 Note: 0.5 is the Occupancy Fraction | Point of sale, Retail - 33 person / 1000 ft2 x 0.5 Back Space- 2 person / 1000 ft2 x 0.5 Front Entry - 66.67 person / 1000 ft2 x 0.5 Note: 0.5 is the Occupancy Fraction
Elevator
Quantity | NA | NA | NA
Motor type
Peak Motor Power (W/elevator)
Heat Gain to Building
Peak Fan/lights Power (W/elevator)
Motor and fan/lights Schedules
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## ConstructionAssembly
Name | Layers | Overall UFactor All Climate Zones | Overall CFactor All Climate Zones | Overall FFactor All Climate Zones | Material Name | Thickness (in) | Conductivity (Btu/h*ft*F) | Density (lb/ft³) | Specific Heat (Btu/lb*F) | Rvalue (ft2*F*hr/Btu)
MetalFrameWall / Metal Framed Wall |  | 0.062 | NA | NA | Stucco - 7/8 in | 0.875 | 0.405 | 115.866 | 0.20063 | 0.18
Outside Layer | Stucco - 7/8 in |  |  |  | Building Paper - 1/16 in | 0.06 | 0.1667 | 70 | 0.3 | 0.03
Layer 2 | Building Paper - 1/16 in |  |  |  | Expanded Polystyrene - EPS - 3 1/3 in | 3.3 | 0.02 | 1.2 | 0.27 | 13.96
Layer 3 | Expanded Polystyrene - EPS - 3 1/3 in |  |  |  | Gypsum Board - 1/2 in | 0.5 | 0.092 | 40 | 0.27 | 0.45
Layer 4 | Air - Metal Wall Framing - 16 or 24 in OC |  |  |  | Composite Wood Frame 24 in OC depth 11.25 in R-30 |  |  |  |  | 30
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Metal Standing Seam - 1/16 in | 0.0625 | 0.333 | 488.22 | 0.12
Roof |  | 0.034 | NA | NA | Expanded Polystyrene - EPS - 6 7/8 in | 6.9 | 0.02 | 1.2 | 0.27 | 28.63
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Expanded Polystyrene - EPS - 1 1/2 in | 1.5 | 0.02 | 1 | 0.27 | 6.25
Layer 2 | Expanded Polystyrene - EPS - 6 7/8 in |  |  |  | Carpet - 3/4 in | 0.75 | 0.0263 | 18 | 0.33 | 2.38
BasementWall |  | NA | 1.14 | NA | Acoustic Tile - 3/4 in | 0.75 | 0.0333 | 18 | 0.19 | 1.89
Layer 2 | Concrete - Solid Grout - 115 lb/ft3 - 8 in |  |  |  | Concrete - Solid Grout - 115 lb/ft3 - 8 in | 8 | 0.433 | 115 | 0.2 | 1.538
Interior wall |  | 0.344 | NA | NA | Stud Wall | 5.5 | 0.705 | 0.08 | 0.24 | 0.65
Outside Layer | Gypsum Board - 1/2 in |  |  |  | Expanded Polystyrene - EPS - 2 in | 2 | 0.02 | 1 | 0.27 | 8.33
Layer 2 | Stud Wall |  |  |  | Concrete - 140 lb/ft3 - 4 in | 4 | 1.128 | 139.78 | 0.22 | 0.3
Layer 3 | Gypsum Board - 1/2 in |  |  |  | Plywood - 1/2 in | 0.5 | 0.0667 | 30 | 0.45 | 0.63
Interior Floor slab |  | 0.238 | NA | NA | Asphalt shingles - 1/4 in | 0.3 | 0.0467 | 69.89 | 0.3 | 0.45
Outside Layer | Concrete - 140 lb/ft3 - 4 in |  |  |  | Air - Metal Wall Framing - 16 or 24 in OC | 5.5 | 0.705 | 0.08 | 0.24 | 0.65
Layer 2 | Carpet - 3/4 in |  |  |  | Compliance Insulation-5 | 0.8 | 0.013 | 1 | 0.27 | 5
Drop Ceiling |  | 0.292 | NA | NA | Expanded Polystyrene - EPS - 4 1/16 in | 4.05 | 0.02 | 1 | 0.27 | 16.88
Outside Layer | Acoustic Tile- 3/4 in. |  |  |  | Compliance Insulation - R5 |  |  |  |  | 5
Floor Slab |  | NA | NA | 0.72 | Compliance insulation R9.83 |  |  |  |  | 9.83
HeavyMassWall |  | 0.063 | NA | NA | Compliance insulation R19.63 |  |  |  |  | 19.63
Outside Layer | Stucco - 7/8 in |  |  |  | Compliance insulation R24.86 |  |  |  |  | 24.86
Layer 2 | Building Paper - 1/16 in |  |  |  | Metal Wall Framing - 16 in OC - R0 |  |  |  |  | 0 | Composite
Layer 3 | Expanded Polystyrene - EPS - 3 1/3 in |  |  |  | Wood Wall Framing - 16 in OC - R0 |  |  |  |  | 0 | Composite
Layer 4 | Concrete - 140 lb/ft3 - 4 in |  |  |  | Metal Wall Single Layer Batt - R10 |  |  |  |  | 10 | Composite
Layer 6 | Gypsum Board - 1/2 in |  |  |  | Metal Wall Double Layer Batt - R13 - R13 |  |  |  |  | 13+13 | Composite
WoodRoof |  | 0.034 | NA | NA | Outside Air Film | ** All construction assembley Ufactors in this tab include air films ** |  |  |  | Rvalue (ft2*F*hr/Btu)
Outside Layer | Asphalt shingles - 1/4 in |  |  |  | Exterior Wall |  |  |  |  | 0.17
Layer 2 | Building Paper - 1/16 in |  |  |  | Roof |  |  |  |  | 0.17
Layer 3 | Plywood - 1/2 in |  |  |  | Exterior Floor |  |  |  |  | 0.17
Layer 4 | Composite Wood Frame 24 in OC R-30 cavity insulation |  |  |  | Underground Wall |  |  |  |  | NA
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Underground Floor |  |  |  |  | NA
MetalFrameWallTest |  | 0.042 | NA | NA | Interior Wall |  |  |  |  | 0.68
Outside Layer | Stucco - 7/8 in |  |  |  | Ceiling |  |  |  |  | 0.92
Layer 2 | Building Paper - 1/16 in |  |  |  | Interior Floor |  |  |  |  | 0.61
Layer 3 | Expanded Polystyrene - EPS - 4 1/16 in |  |  |  | Inside Air Film | ** All construction assembley Ufactors in this tab include air films ** |  |  |  | Rvalue (ft2*F*hr/Btu)
Layer 4 | Compliance Insulation-5 |  |  |  | Exterior Wall |  |  |  |  | 0.68
Layer 5 | Air - Metal Wall Framing - 16 or 24 in OC |  |  |  | Roof |  |  |  |  | 0.61
Layer 6 | Gypsum Board - 1/2 in |  |  |  | Exterior Floor |  |  |  |  | NA
Floor Slab Test |  | NA | NA | 0.46 | Underground Wall |  |  |  |  | NA
RoofTest |  | 0.028 | NA | NA | Underground Floor |  |  |  |  | NA
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Interior Wall |  |  |  |  | NA
Layer 2 | Expanded Polystyrene - EPS - 6 7/8 in |  |  |  | Ceiling |  |  |  |  | NA
Layer 3 | Expanded Polystyrene - EPS - 1 1/2 in |  |  |  | Interior Floor |  |  |  |  | NA
NACM_AtticRfWood |  | 0.049 | NA | NA | Exterior Floor |  |  |  |  | 0.92
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Underground Wall |  |  |  |  | 0.68
Layer 2 | Compliance insulation R19.63 |  |  |  | Underground Floor |  |  |  |  | 0.92
NACM_AtticRfWood_0.39 |  | 0.039 | NA | NA | Interior Floor |  |  |  |  | 0.92
Outside Layer | Metal Standing Seam - 1/16 in
Layer 2 | Compliance insulation R24.86
Attic_Floor |  | 0.039 | NA | NA
Outside Layer | Compliance Insulation R9.83
Layer 2 | Plywood - 5/8 in
Layer 3 | Carpet - 3/4 in

## Zonelvl
LARGE OFFICE
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
WWR20 Case Daylighting | Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
WWR60 Case Daylighting | Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
STAND ALONE RETAIL
Name | Area [ft2] | Conditioned
BACK_SPACE | 4089 | Yes
CORE_RETAIL | 17227 | Yes
POINT_OF_SALE | 1623 | Yes
FRONT_RETAIL | 1623 | Yes
FRONT_ENTRY | 129 | Yes
Conditioned Total | 24692
Unconditioned Total | 0
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2 | SRR3.04 Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Core_Retail | NA | NA | 16742.62 | UnderSkylight | NA | 0.97 |  | 550 lux |  |  | Core_Retail | NA | NA | 16934.71 | UnderSkylight | NA | 0.97 |  | 550 lux
| Point_Of_Sale | 718.07 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux |  |  | Point_Of_Sale | 717.0473 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux
| Front_Retial | 718.07 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux |  |  | Front_Retial | 717.0473 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux
| Front_Entry | 114.3 | NA | NA | In Prim. Daylit Zn | NA | 0.88 |  | 550 lux |  |  | Front_Entry | 85.9294 | NA | NA | In Prim. Daylit Zn | NA | 0.88 |  | 550 lux
Baseline Skylight Layout | [10 empty] | TestCase Skylight Layout
STRIP MALL
Name | Area [ft2] | Conditioned
LGSTORE1 | 3750.0388 | Yes
SMSTORE1 | 1874.9656 | Yes
SMSTORE2 | 1874.9656 | Yes
SMSTORE3 | 1874.9656 | Yes
SMSTORE4 | 1874.9656 | Yes
LGSTORE2 | 3750.0388 | Yes
SMSTORE5 | 1874.9656 | Yes
SMSTORE6 | 1874.9656 | Yes
SMSTORE7 | 1874.9656 | Yes
SMSTORE8 | 1874.9656 | Yes
Total | 18749.7632
Conditioned Total | 18749.7632
Unconditioned Total | 0
Skylight Layout

## Test Criteria
|  | 180 | 181 | 182 | 183 |  | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 |  | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205
Test Run Name | Medium Office 0300CZ-OffMed | 0318006-OffMed-BotOpWinNoInterlock | 0318106-OffMed-BotMidOpWinNoInterlock | 0318206-OffMed-BotMidTopOpWinNoInterlock | 0318306-OffMed-BotMidOpWinNoInterlockTopInterlock | Large Office 0400CZ-OffLrg | 0418406-OffLrg-TES-ChlrPriority | 0418506-OffLrg-TES-StoPriority | 0418606-OffLrg-TES-StoTnkShp | 0418706-OffLrg-TES-StoTnkLoc | 0418806-OffLrg-TES-StoTnkRval | 0418906-OffLrg-TES-StoTnkVol | 0419006-OffLrg-ActiveBeam | 0419106-OffLrg-PassiveBeam | Medium Retail 0500CZ-RetlMed | 0519215-RetlMed-HPWtrHtrPckgdEF2x | 0519315-RetlMed-HPWtrHtrPckgdEF3x | 0519415-RetlMed-HPWtrHtrSplitTnkCprsrOut | 0519515-RetlMed-HPWtrHtrSplitTnkOutCprsrIns | 0519615-RetlMed-UEFConsumerStoGas | 0519715-RetlMed-UEFConsumerInstGas | 0519815-RetlMed-UEFConsumerStoElec | 0519915-RetlMed-UEFConsumerInstElec | 0520015-RetlMed-ExtWall-MtlFrmR0 | 0520115-RetlMed-ExtWall-WdFrmR0 | 0520215-RetlMed-ExtWall-MtlWallSingleLyrBatt-R10 | 0520315-RetlMed-ExtWall-MtlWallDoubleLyrBatt-R13-R13 | 0520415-RetlMed-MiniSplitAC-EER11.2 | 0520515-RetlMed-MiniSplitHP-COP3.3
Baseline |  | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline |  | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun | 0400006-OffLrg-Baserun |  | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline
Prototype Description |  | Bottom Floor with operable windows and no interlock controls. Mid and Top floors fixed windows | Bottom and Mid Floors with operable windows and no interlock controls. Top floor fixed windows | Bottom, Mid and Top floors with operable windows and no interlock controls | Bottom and Mid floors with operable windows and no interlock controls. Top floor with operable windows and interlock controls |  | Thermal Energy Storage Discharge Priority - Chiller | Thermal Energy Storage Discharge Priority - Storage | Thermal Energy Storage Discharge Priority - Storage Tank Shape | Thermal Energy Storage Discharge Priority - Storage Tank Location | Thermal Energy Storage Discharge Priority - Storage Tank R-value | Thermal Energy Storage Discharge Priority - Storage Tanl Storage Volume | Active Beam (Chilled Water) systems serving Mid Floor Zones with DOAS (100% OA) for ventilation and Hot Water Baseboard heating | Passive Beam (Chilled Water) systems serving Mid Floor Zones with DOAS (100% OA) for ventilation and Hot Water Baseboard heating |  | Heat Pump Water Heater Packaged with EF 2x | Heat Pump Water Heater Packaged with EF 3x | Heat Pump Water Heater Split with storage tank and compressor outside | Heat Pump Water Heater Split with storage tank outside and compressor inside | Water Heater with UEF specification - Consumer Storage Gas | Water Heater with UEF specification - Consumer Instantaneous Gas | Water Heater with UEF specification - Consumer Storage Electric | Water Heater with UEF specification - Consumer Instantaneous Electric | Exterior Wall - Metal Frame with R-0 cavity insulation (composite material) | Exterior Wall - Wood Frame with R-0 cavity insulation (composite material) | Exterior Wall - Metal Wall with Single Layer Batt R-10 (composite material) | Exterior Wall - Metal Wall with Double Layer Batt R-13/R-13 (composite material) | Front Retail and Point of Sale Spaces system changed to MiniSplit AC | Front Retail and Point of Sale Spaces system changed to MiniSplit HP (Heat Pump)
Location | CZ000 | CZ06 | CZ06 | CZ06 | CZ06 | CZ000 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ000 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15
Fuel Type
Total Floor Area (sq feet)
Building shape
Aspect Ratio
Number of Floors
Window Fraction (Window-to-Wall Ratio)
Window Locations
Shading Geometry
Azimuth
Thermal Zoning
Floor to floor height (feet)
Floor to ceiling height (feet)
Glazing sill height (feet)
Exterior walls
Construction
Construction Assembly Layers | [15 empty] | 200: Metal Framed Wall Layer #4 change material to: Metal Wall Framing - 16 in OC - R0; 201: Rename 'Metal Framed Wall' to 'Wood Framed Wall' Layer #4 change material to: Wood Wall Framing - 16 in OC - R0; 202: Metal Framed Wall Layer #4 change material to: Metal Wall Single Layer Batt - R10; 203: Metal Framed Wall Layer #4 change material to: Metal Wall Double Layer Batt - R13 - R13
U-factor (Btu / h * ft2 * °F)
Roof
Construction
Construction Assembly Layers
U-factor (Btu / h * ft2 * °F)
Aged Solar Reflectance Aged Thermal Emittance
Dimensions
Tilts and orientations
Window |  | VerticalFenestration | VerticalFenestration | VerticalFenestration | VerticalFenestration
Dimensions
Glass-Type and frame |  | Mfd/NFRC/Operable | Mfd/NFRC/Operable | Mfd/NFRC/Operable | Mfd/NFRC/Operable
U-factor (Btu / h * ft2 * °F) |  | 0.36 | 0.36 | 0.36 | 0.36
SHGC |  | 0.25 | 0.25 | 0.25 | 0.25
Visible transmittance |  | 0.42 | 0.42 | 0.42 | 0.42
Operable area |  | All windows on bottom floor operable | All windows on bottom & mid floors operable | All windows on bottom,mid and top floor operable | All windows on bottom,mid and top floor operable
Interlock Controls |  | None | None | None | Top floor windows with interlock controls
Skylight
Dimensions
Glass-Type and frame
U-factor (Btu / h * ft2 * °F)
SHGC
Visible transmittance
Foundation
Foundation Type
Construction
F factor (Btu / h * ft2 * °F)
Thermal properties for basement walls
Interior Surfaces
Construction
Construction Assembly Layers
Dimensions
Air Barrier System
Infiltration
HVAC System Type
System Type | [12 empty] | Mid Floor System modified to DOAS for ventilationand Active Beam for cooling with Zone System Baseboard Heating | Mid Floor System modified to DOAS for ventilationand Passive Beam (Zone System) for cooling with Zone System Baseboard Heating |  | 204: PointofSale Zone system changed to ZnSys: MiniSplitAC FrontRetail Zone system changed to ZnSys: MiniSplitAC; 205: PointofSale Zone system changed to ZnSys: MiniSplitHP FrontRetail Zone system changed to ZnSys: MiniSplitHP
Heating type | [12 empty] | Mid Floors - Hot Water Zone System Baseboard Heating | Mid Floors - Hot Water Zone System Baseboard Heating |  | 204: Resistance (Electric); 205: HeatPump (Electric) Supplemental Htg Coil - Resistance (Electric)
Cooling type | [12 empty] | DOAS - Chilled Water | DOAS - Chilled Water Zone System Passive Beam (CHW) |  | 204: DirectExpansion; 205: DirectExpansion
Distribution and terminal units | [12 empty] | Active Beam (CHW)
HVAC Sizing
Cooling | [12 empty] | Mid DOAS CoilCooling: 172,588 Btu/h Active Beam (TU) ClgCoil Core MidZn - 125,000 Btu/h PerimMidZn1 - 27,000 Btu/h PerimMidZn2 - 15,000 Btu/h PerimMidZn3 - 18,000 Btu/h PerimMidZn4 -20,000 Btu/h | Mid DOAS CoilCooling: 350,000 Btu/h Passive Beam (ZnSys) ClgCoil Core MidZn - 125,000 Btu/h PerimMidZn1 - 36,000 Btu/h PerimMidZn2 - 18,000 Btu/h PerimMidZn3 - 18,000 Btu/h PerimMidZn4 -24,000 Btu/h |  | 204: See Sizing Values Sheet; 205: See Sizing Values Sheet
Heating | [12 empty] | Mid DOAS CoilHeating: 125,920 Btu/h ZnSys-Baseboard HtgCoil Core MidZn - 10,000 Btu/h PerimMidZn1 - 24,000 Btu/h PerimMidZn2 - 16,000 Btu/h PerimMidZn3 - 24,000 Btu/h PerimMidZn4 -16,000 Btu/h | Mid DOAS CoilHeating: 31,480 Btu/h ZnSys-Baseboard HtgCoil Core MidZn - 10,000 Btu/h PerimMidZn1 - 24,000 Btu/h PerimMidZn2 - 16,000 Btu/h PerimMidZn3 - 24,000 Btu/h PerimMidZn4 -16,000 Btu/h |  | 204: See Sizing Values Sheet; 205: See Sizing Values Sheet
HVAC Efficiency
Cooling | [15 empty] | 204: PointOfSaleZn_CoolingCoil: 11.20 EER/12.90 IEER FrontRetailZn_CoolingCoil: 11.20 EER/12.90 IEER; 205: PointOfSaleZn_CoolingCoil: 11.00 EER/12.20 IEER FrontRetailZn_CoolingCoil: 11.00 EER/12.20 IEER
Heating | [15 empty] | 205: PointOfSaleZn_HeatingCoil: 3.3 COP FrontRetailZn_HeatingCoil: 3.3 COP
HVAC Control
Thermostat Setpoint
Thermostat Setback
Design Supply air temperature
Supply air temperature reset
Chilled water supply temperatures
Chilled water return temperatures
Chilled water supply temperature reset
Condenser Type
Hot water supply temperatures
Hot water supply temperature reset
Economizers
Ventilation | [12 empty] | DOASCV - 100% OA Flow Capacity - 5753 | DOASCV - 100% OA Flow Capacity - 5753 |  | 204: Back_Space: Vent changed to Per Space (cfm): 1,263 cfm; 205: Back_Space: Vent changed to Per Space (cfm): 1,263 cfm
Fan | [12 empty] | Mid DOAS Fan | Mid DOAS Fan |  | 204: MiniSplit Fan - PointOfSale, FrontRetail; 205: MiniSplit Fan - PointOfSale, FrontRetail
Fan type | [12 empty] | ConstantVolume | ConstantVolume |  | 204: ConstantVolume; 205: ConstantVolume
Supply Fan Total Efficiency (%) | [12 empty] | 0.65 | 0.65 |  | 204: 0.6; 205: 0.6
Fan Motor Efficiency | [12 empty] | 0.95 | 0.95 |  | 204: 2.5; 205: 2.5
Supply Fan Pressure Rise | [12 empty] | 4 | 4
Pump | [6 empty] | TES Pump | TES Pump | TES Pump | TES Pump | TES Pump | TES Pump | Boiler 1 Pump | Boiler 1 Pump
Pump Type | [6 empty] | VariableSpeed | VariableSpeed | VariableSpeed | VariableSpeed | VariableSpeed | VariableSpeed | ConstantSpeed | ConstantSpeed
Rated Pump Head | [6 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40
Pump Motor Power per Unit Flow | [6 empty] | 17.4 W/gpm | 17.2 W/gpm | 17.2 W/gpm | 17.2 W/gpm | 17.2 W/gpm | 17.2 W/gpm | 12.0 W/gpm | 12.0 W/gpm
Design Flow Rate (gpm) | [6 empty] | 822.4 | 1644.8 | 1644.8 | 1644.8 | 1644.8 | 1644.8 | 712.4 | 688.8
Nameplate Motor HP | [6 empty] | 20 | 40 | 40 | 40 | 40 | 40 | 15 | 15
Pump Efficiency | [6 empty] | Impeller - 0.7, Motor - 0.93 | Impeller - 0.7, Motor - 0.941 | Impeller - 0.7, Motor - 0.941 | Impeller - 0.7, Motor - 0.941 | Impeller - 0.7, Motor - 0.941 | Impeller - 0.7, Motor - 0.941 | Impeller - 0.7, Motor - 0.900 | Impeller - 0.7, Motor - 0.900
Cooling Tower
Cooling Tower Type
Tower range
Thermal EnergyStorage
TES Type | [6 empty] | ChilledWater | ChilledWater | ChilledWater | ChilledWater | ChilledWater | ChilledWater
Discharge Priority | [6 empty] | Chiller | Storage | Storage | Storage | Storage | Storage
Tank Location | [6 empty] | Indoor | Indoor | Indoor | Underground | Indoor | Indoor
Location Zn Name | [6 empty] | Basement Thermal Zone | Basement Thermal Zone | Basement Thermal Zone | na | Basement Thermal Zone | Basement Thermal Zone
Tank Shape | [6 empty] | Rectangular | Rectangular | VerticalCyclinder | Rectangular | Rectangular | Rectangular
Tank Volume (gal) | [6 empty] | 246515 | 493031 | 493031 | 493031 | 493031 | 394425
Tank Height (ft) | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8
Tank Length to Width Ratio | [6 empty] | 2 | 2 | na | 2 | 2 | 2
Tank R-value (degF-sqft/Btuh) | [6 empty] | 24 | 24 | 24 | 24 | 12 | 24
Chiller | [6 empty] | Chiller 1
Enable during TES Discharge | [6 empty] | Yes (checkbox marked) | na | na | na | na | na
Service Water Heating
SWH type | [15 empty] | 192: HeatPumpPackaged; 193: HeatPumpPackaged; 194: HeatPumpSplit; 195: HeatPumpSplit; 196: Conventional; 197: Conventional; 198: Conventional; 199: Conventional
Fuel type | [15 empty] | 192: Electricity; 193: Electricity; 194: Electricity; 195: Electricity; 196: Gas; 197: Gas; 198: Electricity; 199: Electricity
Storage Capacity (gal) | [15 empty] | 192: 80; 193: 80; 194: 80; 195: 80; 196: 50; 197: 1; 198: 50; 199: 1
Input Rate (Btu/h or kW) | [15 empty] | 192: 4.6 kW; 193: 4.6 kW; 194: 4.6 kW; 195: 4.6 kW; 196: 40,000 Btu/h; 197: 190,000 Btu/h; 198: 8 kW; 199: 8 kW
Thermal efficiency (%)
Recovery Efficiency (%) | [15 empty] | 196: 85; 198: 99; 199: 99
Energy Factor | [15 empty] | 192: 2.33; 193: 3.26; 194: 3.26; 195: 3.26
UEF | [15 empty] | 196: 0.56; 197: 0.85; 198: 0.92; 199: 0.92
First Hour Rating (gal) | [15 empty] | 196: 80; 198: 60
Flow Rate (gal/min) | [15 empty] | 197: 8; 199: 2
Storage Tank Location | [15 empty] | 192: Outside; 193: Outside; 194: Outside; 195: Outside
Compressor Location | [15 empty] | 194: Outside; 195: Inside/Back_Space Thermal Zone
Lighting Load
Lighting power density (W/ft2)
Schedule
Daylighting Controls
Plug load
Electric power density (W/ft2)
Schedule
Occupancy
Average people
Schedule
| 03-OffMed | BotOpWinNoInterlock | BotMidOpWinNoInterlock | BotMidTopOpWinNoInterlock | BotMidOpWinNoInterlockTopInterlock | 04-OffLrg | TES-ChlrPriority | TES-StoPriority | TES-StoTnkShp | TES-StoTnkLoc | TES-StoTnkRval | TES-StoTnkVol | ActiveBeam | PassiveBeam | 05-RetlMed | HPWtrHtrPckgdEF2x | HPWtrHtrPckgdEF3x | HPWtrHtrSplitTnkCprsrOut | HPWtrHtrSplitTnkOutCprsrIns | UEFConsumerStoGas | UEFConsumerInstGas | UEFConsumerStoElec | UEFConsumerInstElec | ExtWall-MtlFrmR0 | ExtWall-WdFrmR0 | ExtWall-MtlWallSingleLyrBatt-R10 | ExtWall-MtlWallDoubleLyrBatt-R13-R13 | MiniSplitAC-EER11.2 | MiniSplitHP-COP3.3
| 000 | 06 | 06 | 06 | 06 | 000 | 06 | 06 | 06 | 06 | 06 | 06 | 06 | 06 | 000 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baserun | -Baserun | -Baserun | -Baserun | -Baserun | -Baserun | -Baserun | -Baserun |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline

## Sizing Values
Sizing Values
|  |  |  | 0300006-OffMed-Baseline | 0400006-OffLrg-Baserun | 0419006-OffLrg-ActiveBeam | 0419106-OffLrg-PassiveBeam | 0500015-RetlMed-Baseline | 0520415-RetlMed-MiniSplitAC-EER11.2 | 0520515-RetlMed-MiniSplitHP-COP3.3
Building |  | Climate Zone | none | 06 | 06 | 06 | 06 | 15 | 15 | 15
Building |  | Weather Station | none | TORRANCE_722955 | TORRANCE_722955 | TORRANCE_722955 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | PALM-SPRINGS-INTL_722868 | PALM-SPRINGS-INTL_722868
Building |  | Zip Code | none | 90505 | 90505 | 90505 | 90505 | 92262 | 92262 | 92262
Units
Chilled Water Loop
Chiller 1 | 7 | Rated Capacity | Btu/h | NA | 8226710 | 5596560 | 6600590 | NA | NA | NA
Chiller 2 | 7 | Rated Capacity | Btu/h | NA | 8226710 | 5596560 | 6600590 | NA | NA | NA
Chiller 1 Pump | 7 | Flow Capacity | gpm | NA | 822.359 | 559.444 | 659.809 | NA | NA | NA
Chiller 1 Pump | 14 | Min Flow Rate | gpm | NA | 246.708 | 167.8 | 197.9 | NA | NA | NA
Chiller 2 Pump | 7 | Flow Capacity | gpm | NA | 822.359 | 559.444 | 659.809 | NA | NA | NA
Chiller 2 Pump | 14 | Min Flow Rate | gpm | NA | 246.708 | 167.8 | 197.9 | NA | NA | NA
Condenser Water Loop
Cooling Tower | 5 | Rated Capacity | Btu/h | NA | 19190400 | 13055081 | 15397175 | NA | NA | NA
Cooling Tower Pump | 7 | Flow Capacity | gpm | NA | 3836.63 | 2610.02 | 3078.3 | NA | NA | NA
Cooling Tower Pump | 9 | Electric Power | kW | NA | 45.8648 | 31.2014 | 36.799 | NA | NA | NA
Hot Water Loop
Boiler 1 | 7 | Rated Capacity | Btu/h | 1250840 | 7329620 | 6173533 | 6173533 | NA | NA | NA
Boiler 1 Pump | 7 | Flow Capacity | gpm | 62.5181 | 366.3 | 308.6 | 308.6 | NA | NA | NA
Boiler 1 Pump | 9 | Electric Power | kW | 0.93421 | 4.3753 | 3.689 | 3.689 | NA | NA | NA
Cooling Coils
CoreZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim1ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim2ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim3ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim4ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
BasementCoilCooling | 7 | Gross Capacity | Btu/h | NA | 1265648.155 | 1265648.155 | 1265648.155 | NA | NA | NA
BottomVAVCoilCooling | 7 | Gross Capacity/Net Capacity | Btu/h | 504732.212 | 1265648.155 | 1265648.155 | 1265648.155 | NA | NA | NA
MidVAVCoilCooling | 7 | Gross Capacity/Net Capacity | Btu/h | 536277.975 | 1265648.155 | NA | NA | NA | NA | NA
HiVAVCoilCooling | 7 | Gross Capacity | Btu/h | NA | 1265648.155 | 1265648.155 | 1265648.155 | NA | NA | NA
TopVAVCoilCooling | 7 | Gross Capacity/Net Capacity | Btu/h | 589905.772 | 1265648.155 | 1265648.155 | 1265648.155 | NA | NA | NA
Mid DOAS CoilCooling | 7 | Gross Capacity | Btu/h | NA | NA | 172588.385 | 350000 | NA | NA | NA
BackSpaceZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | 122673.578 | 122673.578 | 122673.578
PointOfSaleZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | 67529.358 | 48699.056 | 48699.056
FrontRetailZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | 67529.194 | 48698.938 | 48698.938
CoreRetailZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | 516822.13 | 516822.13 | 516822.13
CoreMidZn ClgCoil | 6 | Net Capacity/ Gross Capacity | Btu/h | NA | NA | 125000 | NA | NA | NA | NA
PerimeterMidZn1 ClgCoil | 6 | Net Capacity/ Gross Capacity | Btu/h | NA | NA | 27000 | NA | NA | NA | NA
PerimeterMidZn2 ClgCoil | 6 | Net Capacity/ Gross Capacity | Btu/h | NA | NA | 15000 | NA | NA | NA | NA
PerimeterMidZn3 ClgCoil | 6 | Net Capacity/ Gross Capacity | Btu/h | NA | NA | 18000 | NA | NA | NA | NA
PerimeterMidZn4 ClgCoil | 6 | Net Capacity/ Gross Capacity | Btu/h | NA | NA | 20000 | NA | NA | NA | NA
CoreMid Beam ClgCoil |  | Net Capacity/ Gross Capacity | Btu/h | NA | NA | NA | 125000 | NA | NA | NA
PerimeterMidZn1 Beam ClgCoil |  | Net Capacity/ Gross Capacity | Btu/h | NA | NA | NA | 36000 | NA | NA | NA
PerimeterMidZn2 Beam ClgCoil |  | Net Capacity/ Gross Capacity | Btu/h | NA | NA | NA | 18000 | NA | NA | NA
PerimeterMidZn3 Beam ClgCoil |  | Net Capacity/ Gross Capacity | Btu/h | NA | NA | NA | 18000 | NA | NA | NA
PerimeterMidZn4 Beam ClgCoil |  | Net Capacity/ Gross Capacity | Btu/h | NA | NA | NA | 24000 | NA | NA | NA
|  |  |  | NA | NA | NA | NA | NA | NA | NA
Heating Coils
CoreZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim1ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim2ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim3ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
Perim4ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA
BasementCoilHeating | 7 | Gross Capacity | Btu/h | NA | 1385125.341 | 1385125.341 | 1385125.341 | NA | NA | NA
CoilHeating-BasementReheat | 7 | Gross Capacity | Btu/h | NA | 288567.779 | 288567.779 | 288567.779 | NA | NA | NA
BottomVAVCoilHeating | 7 | Gross Capacity | Btu/h | 97817.103 | 230854.224 | 230854.224 | 230854.224 | NA | NA | NA
CoreBottomReheatCoil | 7 | Gross Capacity | Btu/h | 181032.651 | 512716.216 | 512716.216 | 512716.216 | NA | NA | NA
PerimeterBottom1ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.153 | 63457.654 | 63457.654 | 63457.654 | NA | NA | NA
PerimeterBottom2ReheatCoil | 7 | Gross Capacity | Btu/h | 24160.63 | 40893.887 | 40893.887 | 40893.887 | NA | NA | NA
PerimeterBottom3ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.153 | 63458.077 | 63458.077 | 63458.077 | NA | NA | NA
PerimeterBottom4ReheatCoil | 7 | Gross Capacity | Btu/h | 24158.858 | 40893.614 | 40893.614 | 40893.614 | NA | NA | NA
MidVAVCoilHeating | 7 | Gross Capacity | Btu/h | 97817.103 | 230854.224 | NA | NA | NA | NA | NA
CoreMidReheatCoil | 7 | Gross Capacity | Btu/h | 181032.651 | 512716.216 | NA | NA | NA | NA | NA
Core Mid PTAC Heating | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA
PerimeterMid1ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.153 | 63457.654 | NA | NA | NA | NA | NA
PerimeterMid2ReheatCoil | 7 | Gross Capacity | Btu/h | 24160.63 | 40893.887 | NA | NA | NA | NA | NA
PerimeterMid3ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.153 | 63458.077 | NA | NA | NA | NA | NA
PerimeterMid4ReheatCoil | 7 | Gross Capacity | Btu/h | 24158.858 | 40893.614 | NA | NA | NA | NA | NA
HiVAVCoilHeating | 7 | Gross Capacity | Btu/h | NA | 230854.224 | 230854.224 | 230854.224 | NA | NA | NA
CoreHiReheatCoil | 7 | Gross Capacity | Btu/h | NA | 512716.216 | 512716.216 | 512716.216 | NA | NA | NA
PerimeterHi1ReheatCoil | 7 | Gross Capacity | Btu/h | NA | 63457.654 | 63457.654 | 63457.654 | NA | NA | NA
PerimeterHi2ReheatCoil | 7 | Gross Capacity | Btu/h | NA | 40893.887 | 40893.887 | 40893.887 | NA | NA | NA
PerimeterHi3ReheatCoil | 7 | Gross Capacity | Btu/h | NA | 63458.077 | 63458.077 | 63458.077 | NA | NA | NA
PerimeterHi4ReheatCoil | 7 | Gross Capacity | Btu/h | NA | 40893.614 | 40893.614 | 40893.614 | NA | NA | NA
TopVAVCoilHeating | 7 | Gross Capacity | Btu/h | 107598.813 | 230854.224 | 230854.224 | 230854.224 | NA | NA | NA
CoreTopReheatCoil | 7 | Gross Capacity | Btu/h | 199135.916 | 512716.216 | 512716.216 | 512716.216 | NA | NA | NA
PerimeterTop1ReheatCoil | 7 | Gross Capacity | Btu/h | 41979.469 | 63457.654 | 63457.654 | 63457.654 | NA | NA | NA
PerimeterTop2ReheatCoil | 7 | Gross Capacity | Btu/h | 26576.692 | 40893.887 | 40893.887 | 40893.887 | NA | NA | NA
PerimeterTop3ReheatCoil | 7 | Gross Capacity | Btu/h | 41979.469 | 63458.077 | 63458.077 | 63458.077 | NA | NA | NA
PerimeterTop4ReheatCoil | 7 | Gross Capacity | Btu/h | 26574.744 | 40893.614 | 40893.614 | 40893.614 | NA | NA | NA
BackSpaceZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 89502.642 | 89502.642 | 89502.642
PointOfSaleZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 46190.081 | 35530.831 | 51134.009
FrontRetailZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 46189.969 | 35530.745 | 51133.885
CoreRetailZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 377073.426 | 377073.426 | 377073.426
Mid DOAS CoilHeating |  | Gross Capacity | Btu/h | NA | NA | 125920.486 | 125920.486 | NA | NA | NA
PerimeterMidZn1 BBrd HtgCoil |  | Gross Capacity | Btu/h | NA | NA | 24000 | 24000 | NA | NA | NA
PerimeterMidZn2 BBrd HtgCoil |  | Gross Capacity | Btu/h | NA | NA | 16000 | 16000 | NA | NA | NA
PerimeterMidZn3 BBrd HtgCoil |  | Gross Capacity | Btu/h | NA | NA | 24000 | 24000 | NA | NA | NA
PerimeterMidZn4 BBrd HtgCoil |  | Gross Capacity | Btu/h | NA | NA | 16000 | 16000 | NA | NA | NA
CoreMid BBrd HtgCoil |  | Gross Capacity | Btu/h | NA | NA | 10000 | 10000 | NA | NA | NA
PointOfSaleZn_SuppHeatingCoil |  | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | 35530.831
FrontRetailZn_SuppHeatingCoil |  | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | 35530.745
|  |  |  | NA | NA | NA | NA | NA | NA | NA
Fans
CoreZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim1ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim2ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim3ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim4ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Basement CAVFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | 42188.272 | 42188.272 | 42188.272 | NA | NA | NA
Bottom VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | 17875.932 | 42188.272 | 42188.272 | 42188.272 | NA | NA | NA
Mid VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | 17875.932 | 42188.272 | NA | NA | NA | NA | NA
Hi VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | 42188.272 | 42188.272 | 42188.272 | NA | NA | NA
Top VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | 19663.526 | 42188.272 | 42188.272 | 42188.272 | NA | NA | NA
Mid DOAS Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | 5752.946 | 5752.946 | NA | NA | NA
BackSpaceZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 4089.119 | 4089.119 | 4089.119
PointOfSaleZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 2110.292 | 1623.302 | 1623.302
FrontRetailZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 2110.287 | 1623.298 | 1623.298
CoreRetailZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 17227.404 | 17227.404 | 17227.404
|  |  |  | NA | NA | NA | NA | NA | NA | NA
Terminal Units
CoreZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim1ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim2ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim3ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
Perim4ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
TerminalUnit-Basement | 6 | Primary Air Flow (max air flow rate) | CFM | NA | 42188.272 | 42188.272 | 42188.272 | NA | NA | NA
CoreBottomZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | 10586.705 | 29983.404 | 29983.404 | 29983.404 | NA | NA | NA
PerimeterBottomZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.763 | 3710.974 | 3710.974 | 3710.974 | NA | NA | NA
PerimeterBottomZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.902 | 2391.455 | 2391.455 | 2391.455 | NA | NA | NA
PerimeterBottomZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.763 | 3710.999 | 3710.999 | 3710.999 | NA | NA | NA
PerimeterBottomZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.799 | 2391.439 | 2391.439 | 2391.439 | NA | NA | NA
CoreMidZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | 10586.705 | 29983.404 | 4088.646 | 4088.646 | NA | NA | NA
PerimeterMidZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.763 | 3710.974 | 506.042 | 506.042 | NA | NA | NA
PerimeterMidZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.902 | 2391.455 | 326.108 | 326.108 | NA | NA | NA
PerimeterMidZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.763 | 3710.999 | 506.045 | 506.045 | NA | NA | NA
PerimeterMidZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.799 | 2391.439 | 326.105 | 326.105 | NA | NA | NA
CoreHiZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | 29983.404 | 29983.404 | 29983.404 | NA | NA | NA
PerimeterHiZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | 3710.974 | 3710.974 | 3710.974 | NA | NA | NA
PerimeterHiZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | 2391.455 | 2391.455 | 2391.455 | NA | NA | NA
PerimeterHiZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | 3710.999 | 3710.999 | 3710.999 | NA | NA | NA
PerimeterHiZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | 2391.439 | 2391.439 | 2391.439 | NA | NA | NA
CoreTopZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | 11645.375 | 29983.404 | 29983.404 | 29983.404 | NA | NA | NA
PerimeterTopZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2454.94 | 3710.974 | 3710.974 | 3710.974 | NA | NA | NA
PerimeterTopZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1554.193 | 2391.455 | 2391.455 | 2391.455 | NA | NA | NA
PerimeterTopZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2454.94 | 3710.999 | 3710.999 | 3710.999 | NA | NA | NA
PerimeterTopZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1554.079 | 2391.439 | 2391.439 | 2391.439 | NA | NA | NA
Core Mid DOAS TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA
BackSpaceSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 4089.119 | 4089.119 | 4089.119
PointOfSaleSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 2110.292 | NA | NA
FrontRetailSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 2110.287 | NA | NA
CoreRetailSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 17227.404 | 17227.404 | 17227.404
|  |  |  | NA | NA | NA | NA | NA | NA | NA