## Results
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  |  |  | 9 |  | 10 |  | 10 |  | 11 | [5 empty] | 12 |  | 13 |  |  |  | 14 |  | 16
| Version number | Test Case | Annual TDV EUI (excludes Receptacle, Process, Process Ltg) |  | Site Energy EUI - Electricity (excludes Receptacle, Process, Process Ltg) |  | Site Energy EUI - Natural Gas (excludes Receptacle, Process, Process Ltg) |  | Annual Total End Use Site Energy EUI (excludes Receptacle, Process, Process Ltg) |  | Annual End Use Site Energy EUI | [17 empty] | Unmet Load Hours (UMLH) (Heating + Cooling) |  |  |  | Variation from Baseline | [5 empty] | Pass/Fail
| CBECC-Com 2016.3.0 |  | (kBtu/sqft) |  | (kwh/sqft) |  | (therm/sqft) |  | (kBtu/sqft) |  | Heating (kBtu/sqft) |  | Cooling (kBtu/sqft) |  | Interior Lighting (kBtu/sqft) |  | Gas Equipment (kBtu/sqft) |  | Electric Equipment (kBtu/sqft) |  | Fans (kBtu/sqft) |  | Pumps (kBtu/sqft) |  | Tower (kBtu/sqft) |  | Water Heating (kBtu/sqft) |  | Number of Zones with Total UMLH > 150 |  | Zone Max Total UMLH (Hr/yr) |  | TDV % variation |  | Total End Use Site Energy % Variation |  |  |  |  | Floor Area
13 |  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model
| CBECC-Com 2016.3.0 | 0300006-OffMed-SG-Baseline | 114.538 | 114.538 | 3.67 | 3.67 | 0.033717 | 0.033717 | 15.8933 | 15.8933 | 2.236 | 2.236 | 5.1886 | 5.1886 | 5.7659 | 5.7659 | 0 | 0 | 14.615 | 14.615 | 1.4697 | 1.4697 | 0.097729 | 0.097729 | 0 | 0 | 1.1354 | 1.1354 | 0 | 0 | 0 | 0 | [7 empty] | 53627.8
| CBECC-Com 2016.3.0 | 0315006-OffMed-SG-BotOpWinNoInterlock | 115.297 | 115.297 | 3.6566 | 3.6566 | 0.038497 | 0.038497 | 16.3255 | 16.3255 | 2.714 | 2.714 | 5.1377 | 5.1377 | 5.7659 | 5.7659 | 0 | 0 | 14.615 | 14.615 | 1.4504 | 1.4504 | 0.12198 | 0.12198 | 0 | 0 | 1.1354 | 1.1354 | 0 | 0 | 0 | 0 | 0.6627% | 0.6627% | -0.3653% | -0.0036532 | Yes | Yes | Pass | 53627.8
| CBECC-Com 2016.3.0 | 0315106-OffMed-SG-BotMidOpWinNoInterlock | 116.116 | 116.116 | 3.637 | 3.637 | 0.044045 | 0.044045 | 16.8133 | 16.8133 | 3.2687 | 3.2687 | 5.093 | 5.093 | 5.7659 | 5.7659 | 0 | 0 | 14.615 | 14.615 | 1.4235 | 1.4235 | 0.12674 | 0.12674 | 0 | 0 | 1.1354 | 1.1354 | 0 | 0 | 0 | 0 | 1.378% | 1.378% | -0.8988% | -0.0089883 | Yes | Yes | Pass | 53627.8
| CBECC-Com 2016.3.0 | 0315206-OffMed-SG-BotMidTopOpWinNoInterlock | 116.973 | 116.973 | 3.6168 | 3.6168 | 0.049867 | 0.049867 | 17.3267 | 17.3267 | 3.851 | 3.851 | 5.0477 | 5.0477 | 5.7659 | 5.7659 | 0 | 0 | 14.615 | 14.615 | 1.3944 | 1.3944 | 0.13226 | 0.13226 | 0 | 0 | 1.1354 | 1.1354 | 0 | 0 | 0 | 0 | 2.126% | 2.126% | -1.448% | -0.014476 | Yes | Yes | Pass | 53627.8
x | CBECC-Com 2016.3.0 | 0315306-OffMed-SG-BotMidOpWinNoInterlockTopInterlock | 116.116 | 116.116 | 3.637 | 3.637 | 0.044045 | 0.044045 | 16.8133 | 16.8133 | 3.2687 | 3.2687 | 5.093 | 5.093 | 5.7659 | 5.7659 | 0 | 0 | 14.615 | 14.615 | 1.4235 | 1.4235 | 0.12674 | 0.12674 | 0 | 0 | 1.1354 | 1.1354 | 0 | 0 | 0 | 0 | 1.378% | 1.378% | -0.8988% | -0.0089883 | Yes | Yes | Pass | 53627.8
| CBECC-Com 2016.3.0 | 0400006-OffLrg-Baserun_NDL | 99.8132 | 99.8132 | 3.3896 | 3.3896 | 0.043362 | 0.043362 | 15.9109 | 15.9109 | 3.2192 | 3.2192 | 2.4834 | 2.4834 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7382 | 1.7382 | 1.5717 | 1.5717 | 0.015717 | 0.015717 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | [7 empty] | 498589
| CBECC-Com 2016.3.0 | 0415006-OffLrg-TES-ChlrPriority_NDL | 100.147 | 100.147 | 3.4497 | 3.4497 | 0.043994 | 0.043994 | 16.1676 | 16.1676 | 3.2824 | 3.2824 | 2.5187 | 2.5187 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7287 | 1.7287 | 1.7408 | 1.7408 | 0.014444 | 0.014444 | 1.1167 | 1.1167 | 0 | 0 | 0.5 | 0.5 | 0.3344% | 0.3344% | 1.775% | 0.017751 | Yes | Yes | Pass | 498589
x | CBECC-Com 2016.3.0 | 0415106-OffLrg-TES-StoPriority_NDL | 91.4965 | 91.4965 | 3.4698 | 3.4698 | 0.044632 | 0.044632 | 16.3183 | 16.3183 | 3.3462 | 3.3462 | 2.6536 | 2.6536 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7194 | 1.7194 | 1.7006 | 1.7006 | 0.015865 | 0.015865 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | -8.332% | -8.332% | 2.367% | 0.023669 | No | No | Pass | 498589
| CBECC-Com 2016.3.0 | 0400006-OffLrg-Baserun_NDL | 99.8132 | 99.8132 | 3.3896 | 3.3896 | 0.043362 | 0.043362 | 15.9109 | 15.9109 | 3.2192 | 3.2192 | 2.4834 | 2.4834 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7382 | 1.7382 | 1.5717 | 1.5717 | 0.015717 | 0.015717 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | [7 empty] | 498589
x | CBECC-Com 2016.3.0 | 0416006-OffLrg-ActiveBeam_NDL | 108.394 | 108.394 | 3.7907 | 3.7907 | 0.059242 | 0.059242 | 18.841 | 18.841 | 4.8072 | 4.8072 | 3.4845 | 3.4845 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 2.0878 | 2.0878 | 1.5539 | 1.5539 | 0.024947 | 0.024947 | 1.1167 | 1.1167 | 2 | 2 | 348.75 | 348.75 | 8.597% | 8.597% | 11.83% | 0.11834 | Yes | Yes | Pass | 498589
| CBECC-Com 2016.3.0 | 0416106-OffLrg-PassiveBeam_NDL | 110.383 | 110.383 | 3.8509 | 3.8509 | 0.059178 | 0.059178 | 19.0263 | 19.0263 | 4.8008 | 4.8008 | 3.4759 | 3.4759 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 2.0881 | 2.0881 | 1.7566 | 1.7566 | 0.022406 | 0.022406 | 1.1167 | 1.1167 | 3 | 3 | 323.25 | 323.25 | 10.59% | 10.59% | 13.61% | 0.13609 | Yes | Yes | Pass | 498589
| CBECC-Com 2016.3.0 | 0415106-OffLrg-TES-StoPriority_NDL | 91.4965 | 91.4965 | 3.4698 | 3.4698 | 0.044632 | 0.044632 | 16.3183 | 16.3183 | 3.3462 | 3.3462 | 2.6536 | 2.6536 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7194 | 1.7194 | 1.7006 | 1.7006 | 0.015865 | 0.015865 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | [7 empty] | 498589
| CBECC-Com 2016.3.0 | 0415206-OffLrg-TES-StoTnkShp_NDL | 91.4923 | 91.4923 | 3.4698 | 3.4698 | 0.044594 | 0.044594 | 16.314 | 16.314 | 3.3424 | 3.3424 | 2.6529 | 2.6529 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7198 | 1.7198 | 1.7004 | 1.7004 | 0.015863 | 0.015863 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | -0.00459% | -0.00459% | 0% | 0 | No | No | Pass | 498589
| CBECC-Com 2016.3.0 | 0415306-OffLrg-TES-StoTnkLoc_NDL | 91.5917 | 91.5917 | 3.4898 | 3.4898 | 0.043364 | 0.043364 | 16.2212 | 16.2212 | 3.2194 | 3.2194 | 2.6674 | 2.6674 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7394 | 1.7394 | 1.6964 | 1.6964 | 0.016072 | 0.016072 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | 0.104% | 0.104% | 0.578% | 0.0057803 | Yes | Yes | Pass | 498589
x | CBECC-Com 2016.3.0 | 0415406-OffLrg-TES-StoTnkRval_NDL | 91.7232 | 91.7232 | 3.4898 | 3.4898 | 0.045875 | 0.045875 | 16.4638 | 16.4638 | 3.4705 | 3.4705 | 2.6727 | 2.6727 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7122 | 1.7122 | 1.7097 | 1.7097 | 0.016 | 0.016 | 1.1167 | 1.1167 | 0 | 0 | 1 | 1 | 0.2478% | 0.2478% | 0.578% | 0.0057803 | Yes | Yes | Pass | 498589
x | CBECC-Com 2016.3.0 | 0415506-OffLrg-TES-StoTnkVol_NDL | 91.4839 | 91.4839 | 3.4698 | 3.4698 | 0.044349 | 0.044349 | 16.2903 | 16.2903 | 3.3178 | 3.3178 | 2.6533 | 2.6533 | 5.7659 | 5.7659 | 0 | 0 | 14.6453 | 14.6453 | 1.7225 | 1.7225 | 1.698 | 1.698 | 0.016001 | 0.016001 | 1.1167 | 1.1167 | 0 | 0 | 0 | 0 | -0.01377% | -0.01377% | 0% | 0 | No | No | Pass | 498589
| CBECC-Com 2016.3.0 | 0500015-RetlMed-SG-Baseline | 335.248 | 335.248 | 12.3259 | 12.3259 | 0.023156 | 0.023156 | 44.3727 | 44.3727 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | [7 empty] | 24563.1
x | CBECC-Com 2016.3.0 | 0515015-RetlMed-SG-HPWtrHtrPckgdEF2x | 337.847 | 337.847 | 12.5908 | 12.5908 | 0.0026341 | 0.0026341 | 43.225 | 43.225 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7622 | 14.7622 | 0 | 0 | 0 | 0 | 0.84691 | 0.84691 | 0 | 0 | 0 | 0 | 0.7752% | 0.7752% | 2.15% | 0.021495 | Yes | Yes | Pass | 24563.1
x | CBECC-Com 2016.3.0 | 0515115-RetlMed-SG-HPWtrHtrPckgdEF3x | 336.171 | 336.171 | 12.5101 | 12.5101 | 0.0026341 | 0.0026341 | 42.9494 | 42.9494 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7447 | 14.7447 | 0 | 0 | 0 | 0 | 0.58885 | 0.58885 | 0 | 0 | 0 | 0 | 0.2753% | 0.2753% | 1.494% | 0.014942 | Yes | Yes | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0515215-RetlMed-SG-HPWtrHtrSplitTnkCprsrOut | 335.914 | 335.914 | 12.4979 | 12.4979 | 0.0026341 | 0.0026341 | 42.908 | 42.908 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7447 | 14.7447 | 0 | 0 | 0 | 0 | 0.54742 | 0.54742 | 0 | 0 | 0 | 0 | 0.1987% | 0.1987% | 1.395% | 0.013955 | Yes | Yes | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0515315-RetlMed-SG-HPWtrHtrSplitTnkOutCprsrIns | 334.557 | 334.557 | 12.4366 | 12.4366 | 0.0034211 | 0.0034211 | 42.7774 | 42.7774 | 0.34202 | 0.34202 | 14.1578 | 14.1578 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7437 | 14.7437 | 0 | 0 | 0 | 0 | 0.5482 | 0.5482 | 0 | 0 | 0 | 0 | -0.2061% | -0.2061% | 0.8984% | 0.008984 | No | No | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0500015-RetlMed-SG-Baseline | 335.248 | 335.248 | 12.3259 | 12.3259 | 0.023156 | 0.023156 | 44.3727 | 44.3727 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | [7 empty] | 24563.1
| CBECC-Com 2016.3.0 | 0515415-RetlMed-SG-UEFConsumerStoGas | 335.841 | 335.841 | 12.3259 | 12.3259 | 0.027278 | 0.027278 | 44.7848 | 44.7848 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.4638 | 2.4638 | 0 | 0 | 0 | 0 | 0.1769% | 0.1769% | 0% | 0 | Yes | Yes | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0515515-RetlMed-SG-UEFConsumerInstGas | 334.937 | 334.937 | 12.3259 | 12.3259 | 0.020995 | 0.020995 | 44.1567 | 44.1567 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 1.8357 | 1.8357 | 0 | 0 | 0 | 0 | -0.09277% | -0.09277% | 0% | 0 | No | No | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0515615-RetlMed-SG-UEFConsumerStoElec | 343.363 | 343.363 | 12.8052 | 12.8052 | 0.0026341 | 0.0026341 | 43.9564 | 43.9564 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 1.6354 | 1.6354 | 0 | 0 | 0 | 0 | 2.421% | 2.421% | 3.889% | 0.038885 | Yes | Yes | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0515715-RetlMed-SG-UEFConsumerInstElec | 343.784 | 343.784 | 12.8231 | 12.8231 | 0.0026341 | 0.0026341 | 44.0173 | 44.0173 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 1.6964 | 1.6964 | 0 | 0 | 0 | 0 | 2.546% | 2.546% | 4.034% | 0.040335 | Yes | Yes | Pass | 24563.1
x | CBECC-Com 2016.3.0 | 0500015-RetlMed-SG-Baseline | 335.248 | 335.248 | 12.3259 | 12.3259 | 0.023156 | 0.023156 | 44.3727 | 44.3727 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | [7 empty] | 24563.1
x | CBECC-Com 2016.3.0 | 0516015-RetlMed-SG-ExtWall-MtlFrmR0 | 335.25 | 335.25 | 12.326 | 12.326 | 0.023157 | 0.023157 | 44.3732 | 44.3732 | 0.26345 | 0.26345 | 14.3672 | 14.3672 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | 0.0005966% | 0.0005966% | 0.0006606% | 6.6058e-06 | Yes | Yes | Pass | 24563.1
x | CBECC-Com 2016.3.0 | 0516115-RetlMed-SG-ExtWall-WdFrmR0 | 335.168 | 335.168 | 12.3238 | 12.3238 | 0.02314 | 0.02314 | 44.3641 | 44.3641 | 0.26169 | 0.26169 | 14.3599 | 14.3599 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | -0.02386% | -0.02386% | -0.01684% | -0.00016845 | No | No | Pass | 24563.1
x | CBECC-Com 2016.3.0 | 0516215-RetlMed-SG-ExtWall-MtlWallSingleLyrBatt-R10 | 333.483 | 333.483 | 12.2791 | 12.2791 | 0.022841 | 0.022841 | 44.1816 | 44.1816 | 0.23187 | 0.23187 | 14.2074 | 14.2074 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7049 | 14.7049 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | -0.5265% | -0.5265% | -0.3795% | -0.0037951 | No | No | Pass | 24563.1
x | CBECC-Com 2016.3.0 | 0516315-RetlMed-SG-ExtWall-MtlWallDoubleLyrBatt-R13-R13 | 331.964 | 331.964 | 12.2386 | 12.2386 | 0.022608 | 0.022608 | 44.0201 | 44.0201 | 0.20853 | 0.20853 | 14.0691 | 14.0691 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7049 | 14.7049 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | -0.9796% | -0.9796% | -0.7081% | -0.0070815 | No | No | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0500015-RetlMed-SG-Baseline | 335.248 | 335.248 | 12.3259 | 12.3259 | 0.023156 | 0.023156 | 44.3727 | 44.3727 | 0.26334 | 0.26334 | 14.3668 | 14.3668 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 14.7051 | 14.7051 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | [7 empty] | 24563.1
x | CBECC-Com 2016.3.0 | 0517015-RetlMed-SG-MiniSplitAC-EER11.2 | 326.48 | 326.48 | 11.9504 | 11.9504 | 0.025007 | 0.025007 | 43.2766 | 43.2766 | 0.45187 | 0.45187 | 14.4814 | 14.4814 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 13.3059 | 13.3059 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | -2.615% | -2.615% | -3.046% | -0.030463 | No | No | Pass | 24563.1
| CBECC-Com 2016.3.0 | 0517115-RetlMed-SG-MiniSplitHP-COP3.3 | 327.395 | 327.395 | 11.9822 | 11.9822 | 0.025007 | 0.025007 | 43.3851 | 43.3851 | 0.45004 | 0.45004 | 14.5417 | 14.5417 | 12.9857 | 12.9857 | 0 | 0 | 10.8469 | 10.8469 | 13.3559 | 13.3559 | 0 | 0 | 0 | 0 | 2.0517 | 2.0517 | 0 | 0 | 0 | 0 | -2.342% | -2.342% | -2.788% | -0.02788 | No | No | Pass | 24563.1

## Sheet1 (hidden)
COPY BatchResults.csv values from cell A1 and paste here @cell B2 |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73
|  |  | 6: Analysis:; 10: Proposed Model:; 13: Proposed Model; 26: Proposed Model; 39: Proposed Model; 52: Proposed Model; 65: Proposed Model; 68: Proposed Model | Standard Model: |  |  | Standard Model | [12 empty] | Standard Model | [12 empty] | Standard Model | [12 empty] | Standard Model | [12 empty] | Standard Model |  |  | Standard Model | [5 empty] | Proposed Model | [12 empty] | Standard Model | [12 empty] | Calling | Compliance |  |  |  | Secondary
|  |  | 4: Conditioned Floor; 5: Total Floor; 8: Pass /; 9: Compliance; 10: Elapsed; 13: Electric Energy Consumption (kWh); 26: Natural Gas Energy Consumption (therms); 39: Propane Energy Consumption (MBtu); 52: Time Dependent Valuation (kTDV/ft2); 65: TDV by Fuel (kTDV/ft2); 68: Cooling Unmet Load Hours; 71: Heating Unmet Load Hours | Elapsed |  |  | Electric Energy Consumption (kWh) | [12 empty] | Natural Gas Energy Consumption (therms) | [12 empty] | Propane Energy Consumption (MBtu) | [12 empty] | Time Dependent Valuation (kTDV/ft2) | [12 empty] | TDV by Fuel (kTDV/ft2) |  |  | Cooling Unmet Load Hours |  |  | Heating Unmet Load Hours |  |  | Generation Coincident Peak Demand (kW) | [12 empty] | Generation Coincident Peak Demand (kW) | [12 empty] | Application | Manager | Ruleset | OpenStudio | EnergyPlus | Simulation
Floor Area | Start Date & Time | Filename (saved to) | Run Title | Weather Station | Area (SqFt) | Area (SqFt) | Analysis Type | Elapsed Time | Fail | Margin | Time | Rule Eval Status | Simulation Status | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Electric | Natural Gas | Propane | Zone Max | Zone Name | Num Zones Exceed Max | Zone Max | Zone Name | Num Zones Exceed Max | Time | Rule Eval Status | Simulation Status | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Electric | Natural Gas | Propane | Zone Max | Zone Name | Num Zones Exceed Max | Zone Max | Zone Name | Num Zones Exceed Max | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Spc Heating | Spc Cooling | Indoor Fans | Ht Reject | Pumps & Misc | Domestic Hot Water | Indoor Lighting | Comp Total | Receptacle | Process | Other Ltg | Proc Mtrs | TOTAL | Version | Version | Version | Version | Version | Version | Weather File Path | Project Path
| 2017-09-26 19:48 | 0300006-OffMed-SG-Baseline | 0300006-eline | TORRANCE_722955 | 53627.8 | 53627.8 | Title24Compliance | 1:10 | PASS | 4.38 | -- | -- | Successful (130 warnings) | 7.802 | 81547.6 | 23099.1 | 0 | 1535.98 | 0 | 90621.7 | 196812 | 229701 | 0 | 0 | 0 | 426514 | 1199.12 | 0 | 0 | 0 | 0 | 609.044 | 0 | 1808.16 | 0 | 0 | 0 | 0 | 1808.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7039 | 55.4871 | 11.1669 | 0 | 0.48468 | 1.6342 | 42.0613 | 114.538 | 109.034 | 0 | 0 | 0 | 223.572 | 218.236 | 5.3356 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (117 warnings) | 9.135 | 77690.3 | 37473.3 | 0 | 1333.31 | 0 | 90621.7 | 207128 | 229701 | 0 | 0 | 0 | 436829 | 1609.08 | 0 | 0 | 0 | 0 | 640.427 | 0 | 2249.51 | 0 | 0 | 0 | 0 | 2249.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9406 | 51.7639 | 18.0086 | 0 | 0.4216 | 1.7183 | 42.0613 | 118.914 | 109.034 | 0 | 0 | 0 | 227.948 | 221.292 | 6.656 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 19:49 | 0315006-OffMed-SG-BotOpWinNoInterlock | 0315006-rlock | TORRANCE_722955 | 53627.8 | 53627.8 | Title24Compliance | 1:10 | PASS | 3.03 | -- | -- | Successful (130 warnings) | 9.47 | 80748.3 | 22796.3 | 0 | 1917.18 | 0 | 90621.7 | 196093 | 229701 | 0 | 0 | 0 | 425794 | 1455.47 | 0 | 0 | 0 | 0 | 609.045 | 0 | 2064.52 | 0 | 0 | 0 | 0 | 2064.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4671 | 55.4256 | 11.0986 | 0 | 0.60985 | 1.6342 | 42.0613 | 115.297 | 109.034 | 0 | 0 | 0 | 224.331 | 218.232 | 6.0983 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (117 warnings) | 9.5607 | 76785 | 36870.8 | 0 | 1383.76 | 0 | 90621.7 | 205671 | 229701 | 0 | 0 | 0 | 435372 | 1681.62 | 0 | 0 | 0 | 0 | 640.427 | 0 | 2322.05 | 0 | 0 | 0 | 0 | 2322.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1614 | 51.2506 | 17.7023 | 0 | 0.43771 | 1.7183 | 42.0613 | 118.332 | 109.034 | 0 | 0 | 0 | 227.366 | 220.489 | 6.8766 | 0 | 0 |  | 0 | 2 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 19:50 | 0315106-OffMed-SG-BotMidOpWinNoInterlock | 0315106-rlock | TORRANCE_722955 | 53627.8 | 53627.8 | Title24Compliance | 1:11 | PASS | 1.61 | -- | -- | Successful (130 warnings) | 11.4055 | 80044.9 | 22373.1 | 0 | 1991.88 | 0 | 90621.7 | 195043 | 229701 | 0 | 0 | 0 | 424744 | 1752.96 | 0 | 0 | 0 | 0 | 609.045 | 0 | 2362.01 | 0 | 0 | 0 | 0 | 2362.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3304 | 55.4674 | 10.9883 | 0 | 0.63416 | 1.6342 | 42.0613 | 116.116 | 109.034 | 0 | 0 | 0 | 225.15 | 218.189 | 6.961 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (117 warnings) | 10.1312 | 75779.4 | 36117.1 | 0 | 1427 | 0 | 90621.7 | 203955 | 229701 | 0 | 0 | 0 | 433657 | 1778.27 | 0 | 0 | 0 | 0 | 640.426 | 0 | 2418.7 | 0 | 0 | 0 | 0 | 2418.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4495 | 50.7019 | 17.3362 | 0 | 0.4515 | 1.7183 | 42.0613 | 117.719 | 109.034 | 0 | 0 | 0 | 226.753 | 219.588 | 7.1646 | 0 | 0 |  | 0 | 0.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 19:52 | 0315206-OffMed-SG-BotMidTopOpWinNoInterlock | 0315206-rlock | TORRANCE_722955 | 53627.8 | 53627.8 | Title24Compliance | 1:11 | PASS | 0.09 | -- | -- | Successful (130 warnings) | 13.4373 | 79334 | 21915.2 | 0 | 2078.73 | 0 | 90621.7 | 193963 | 229701 | 0 | 0 | 0 | 423665 | 2065.24 | 0 | 0 | 0 | 0 | 609.045 | 0 | 2674.28 | 0 | 0 | 0 | 0 | 2674.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2256 | 55.5669 | 10.8244 | 0 | 0.66103 | 1.6342 | 42.0613 | 116.973 | 109.034 | 0 | 0 | 0 | 226.007 | 218.152 | 7.8555 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (117 warnings) | 10.7288 | 74941.1 | 35261.7 | 0 | 1479.73 | 0 | 90621.7 | 202315 | 229701 | 0 | 0 | 0 | 432016 | 1879.47 | 0 | 0 | 0 | 0 | 640.426 | 0 | 2519.89 | 0 | 0 | 0 | 0 | 2519.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7466 | 50.2146 | 16.8507 | 0 | 0.46824 | 1.7183 | 42.0613 | 117.06 | 109.034 | 0 | 0 | 0 | 226.094 | 218.632 | 7.4615 | 0 | 0 |  | 0 | 1 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 19:53 | 0315306-OffMed-SG-BotMidOpWinNoInterlockTopInterlock | 0315306-rlock | TORRANCE_722955 | 53627.8 | 53627.8 | Title24Compliance | 1:11 | PASS | 0.95 | -- | -- | Successful (130 warnings) | 11.4055 | 80044.9 | 22373.1 | 0 | 1991.88 | 0 | 90621.7 | 195043 | 229701 | 0 | 0 | 0 | 424744 | 1752.96 | 0 | 0 | 0 | 0 | 609.045 | 0 | 2362.01 | 0 | 0 | 0 | 0 | 2362.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3304 | 55.4674 | 10.9883 | 0 | 0.63416 | 1.6342 | 42.0613 | 116.116 | 109.034 | 0 | 0 | 0 | 225.15 | 218.189 | 6.961 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (117 warnings) | 10.7288 | 74941.1 | 35261.7 | 0 | 1479.73 | 0 | 90621.7 | 202315 | 229701 | 0 | 0 | 0 | 432016 | 1879.47 | 0 | 0 | 0 | 0 | 640.426 | 0 | 2519.89 | 0 | 0 | 0 | 0 | 2519.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7466 | 50.2146 | 16.8507 | 0 | 0.46824 | 1.7183 | 42.0613 | 117.06 | 109.034 | 0 | 0 | 0 | 226.094 | 218.632 | 7.4615 | 0 | 0 |  | 0 | 1 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 19:56 | 0400006-OffLrg-Baserun_NDL | 0400006-n_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 2:59 | PASS | 1.68 | -- | -- | Successful (136 warnings) | 104.436 | 362883 | 253994 | 2296.58 | 229661 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3830000 | 16051.1 | 0 | 0 | 0 | 0 | 5568.97 | 0 | 21620 | 0 | 0 | 0 | 0 | 21620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0381 | 27.1072 | 12.61 | 0.28352 | 11.1058 | 1.6072 | 42.0613 | 99.8132 | 109.034 | 0 | 0 | 0 | 208.847 | 202.205 | 6.6418 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:01 | 0415006-OffLrg-TES-ChlrPriority_NDL | 0415006-y_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 5:01 | PASS | 1.36 | -- | -- | Successful (137 warnings) | 106.483 | 368033 | 252596 | 2110.58 | 254376 | 0 | 842528 | 1720000 | 2140000 | 0 | 0 | 0 | 3860000 | 16365.8 | 0 | 0 | 0 | 0 | 5568.97 | 0 | 21934.8 | 0 | 0 | 0 | 0 | 21934.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1326 | 26.6709 | 12.5524 | 0.26344 | 11.8591 | 1.6072 | 42.0613 | 100.147 | 109.034 | 0 | 0 | 0 | 209.181 | 202.445 | 6.7362 | 0 | 0.5 | Perimeter_top_ZN_4 Thermal Zone | 0 | 0 |  | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:06 | 0415106-OffLrg-TES-StoPriority_NDL | 0415106-y_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 4:56 | PASS | 10 | -- | -- | Successful (143 warnings) | 108.554 | 387743 | 251246 | 2318.18 | 248499 | 0 | 842528 | 1730000 | 2140000 | 0 | 0 | 0 | 3870000 | 16684 | 0 | 0 | 0 | 0 | 5568.98 | 0 | 22253 | 0 | 0 | 0 | 0 | 22253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2281 | 19.7463 | 12.4602 | 0.15916 | 10.2343 | 1.6072 | 42.0613 | 91.4965 | 109.034 | 0 | 0 | 0 | 200.53 | 193.699 | 6.8317 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:11 | 0415206-OffLrg-TES-StoTnkShp_NDL | 0415206-p_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 4:57 | PASS | 10.02 | -- | -- | Successful (143 warnings) | 108.431 | 387651 | 251298 | 2317.95 | 248469 | 0 | 842528 | 1730000 | 2140000 | 0 | 0 | 0 | 3870000 | 16665.1 | 0 | 0 | 0 | 0 | 5568.98 | 0 | 22234.1 | 0 | 0 | 0 | 0 | 22234.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2226 | 19.745 | 12.4637 | 0.15918 | 10.2333 | 1.6072 | 42.0613 | 91.4923 | 109.034 | 0 | 0 | 0 | 200.526 | 193.7 | 6.8262 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:16 | 0415306-OffLrg-TES-StoTnkLoc_NDL | 0415306-c_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 4:55 | PASS | 9.9 | -- | -- | Successful (143 warnings) | 104.441 | 389762 | 254167 | 2348.52 | 247876 | 0 | 842528 | 1740000 | 2140000 | 0 | 0 | 0 | 3870000 | 16051.9 | 0 | 0 | 0 | 0 | 5568.97 | 0 | 21620.8 | 0 | 0 | 0 | 0 | 21620.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0383 | 19.8776 | 12.6307 | 0.16114 | 10.2154 | 1.6072 | 42.0613 | 91.5917 | 109.034 | 0 | 0 | 0 | 200.626 | 193.984 | 6.642 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:21 | 0415406-OffLrg-TES-StoTnkRval_NDL | 0415406-l_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 4:49 | PASS | 9.77 | -- | -- | Successful (143 warnings) | 112.586 | 390547 | 250194 | 2337.91 | 249827 | 0 | 842528 | 1740000 | 2140000 | 0 | 0 | 0 | 3870000 | 17303.8 | 0 | 0 | 0 | 0 | 5568.99 | 0 | 22872.8 | 0 | 0 | 0 | 0 | 22872.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4056 | 19.8193 | 12.3846 | 0.15957 | 10.2855 | 1.6072 | 42.0613 | 91.7232 | 109.034 | 0 | 0 | 0 | 200.757 | 193.748 | 7.0091 | 0 | 0 |  | 0 | 1 | Basement Thermal Zone | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:26 | 0415506-OffLrg-TES-StoTnkVol_NDL | 0415506-l_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 4:55 | PASS | 10.01 | -- | -- | Successful (143 warnings) | 107.635 | 387712 | 251698 | 2338.03 | 248116 | 0 | 842528 | 1730000 | 2140000 | 0 | 0 | 0 | 3870000 | 16542.7 | 0 | 0 | 0 | 0 | 5568.98 | 0 | 22111.7 | 0 | 0 | 0 | 0 | 22111.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1862 | 19.7598 | 12.4879 | 0.16002 | 10.2215 | 1.6072 | 42.0613 | 91.4839 | 109.034 | 0 | 0 | 0 | 200.518 | 193.728 | 6.7898 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:34 | 0416006-OffLrg-ActiveBeam_NDL | 0416006-m_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 7:30 | FAIL | -6.9 | -- | -- | Successful (6 severe errors, 153 warnings) | 157.057 | 509165 | 305080 | 3645.26 | 227061 | 0 | 842528 | 1890000 | 2140000 | 0 | 0 | 0 | 4020000 | 23968.5 | 0 | 0 | 0 | 0 | 5568.97 | 0 | 29537.5 | 0 | 0 | 0 | 0 | 29537.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2362 | 32.4985 | 14.3823 | 0.35118 | 10.2571 | 1.6072 | 42.0613 | 108.394 | 109.034 | 0 | 0 | 0 | 217.428 | 208.59 | 8.8374 | 0 | 348 | Perimeter_mid_ZN_1 Thermal Zone | 2 | 0.75 | Core_mid Thermal Zone | 0 | -- | -- | Successful (141 warnings) | 90.5726 | 291392 | 409694 | 39914.9 | 103758 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15445.9 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 21013.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9347 | 23.128 | 20.9405 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.509 | 109.034 | 0 | 0 | 0 | 210.543 | 204.005 | 6.5385 | 0 | 0 |  | 0 | 1.5 | Perimeter_top_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:40 | 0416106-OffLrg-PassiveBeam_NDL | 0416106-m_NDL | TORRANCE_722955 | 498589 | 498589 | Title24Compliance | 5:56 | FAIL | -8.88 | -- | -- | Successful (5 severe errors, 153 warnings) | 156.763 | 507901 | 305112 | 3274.02 | 256673 | 0 | 842528 | 1920000 | 2140000 | 0 | 0 | 0 | 4050000 | 23936.8 | 0 | 0 | 0 | 0 | 5568.98 | 0 | 29505.7 | 0 | 0 | 0 | 0 | 29505.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2149 | 33.1385 | 14.3813 | 0.32896 | 11.6505 | 1.6072 | 42.0613 | 110.383 | 109.034 | 0 | 0 | 0 | 219.417 | 210.601 | 8.816 | 0 | 301.5 | Perimeter_mid_ZN_1 Thermal Zone | 3 | 21.75 | Core_mid Thermal Zone | 0 | -- | -- | Successful (141 warnings) | 90.4442 | 291391 | 409709 | 39914.9 | 103757 | 0 | 842528 | 1690000 | 2140000 | 0 | 0 | 0 | 3820000 | 15426.6 | 0 | 0 | 0 | 0 | 5567.39 | 0 | 20994 | 0 | 0 | 0 | 0 | 20994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9281 | 23.128 | 20.9411 | 3.0735 | 5.7646 | 1.6068 | 42.0613 | 101.503 | 109.034 | 0 | 0 | 0 | 210.537 | 204.005 | 6.5318 | 0 | 0 |  | 0 | 2 | Perimeter_mid_ZN_3 Thermal Zone | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:40 | 0500015-RetlMed-SG-Baseline | 0500015-eline | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:45 | FAIL | -77.58 | -- | -- | Successful (83 warnings) | 0 | 103423 | 105858 | 0 | 0 | 0 | 93480.7 | 302762 | 77659.3 | 0 | 424.545 | 0 | 380846 | 64.7005 | 0 | 0 | 0 | 0 | 504.09 | 0 | 568.791 | 0 | 0 | 0 | 0 | 568.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 99.9842 | 0 | 0 | 2.9765 | 93.0919 | 335.248 | 77.5842 | 0 | 0.42278 | 0 | 413.255 | 409.857 | 3.3986 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 547.347 | 0 | 833.922 | 0 | 0 | 0 | 0 | 833.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2313 | 93.0919 | 257.659 | 77.5842 | 0 | 0.42278 | 0 | 335.666 | 330.407 | 5.2587 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:41 | 0515015-RetlMed-SG-HPWtrHtrPckgdEF2x | 0515015-dEF2x | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:47 | FAIL | -80.14 | -- | -- | Successful (88 warnings) | 0 | 103423 | 106269 | 0 | 0 | 6096.7 | 93480.7 | 309270 | 77659.3 | 0 | 424.545 | 0 | 387353 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 100.319 | 0 | 0 | 5.2401 | 93.0919 | 337.847 | 77.5842 | 0 | 0.42278 | 0 | 415.854 | 415.431 | 0.42212 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 554.362 | 0 | 840.937 | 0 | 0 | 0 | 0 | 840.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2723 | 93.0919 | 257.7 | 77.5842 | 0 | 0.42278 | 0 | 335.707 | 330.407 | 5.2998 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:42 | 0515115-RetlMed-SG-HPWtrHtrPckgdEF3x | 0515115-dEF3x | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -78.47 | -- | -- | Successful (88 warnings) | 0 | 103423 | 106143 | 0 | 0 | 4238.98 | 93480.7 | 307286 | 77659.3 | 0 | 424.545 | 0 | 385370 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 100.217 | 0 | 0 | 3.666 | 93.0919 | 336.171 | 77.5842 | 0 | 0.42278 | 0 | 414.178 | 413.756 | 0.42212 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 554.362 | 0 | 840.937 | 0 | 0 | 0 | 0 | 840.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2723 | 93.0919 | 257.7 | 77.5842 | 0 | 0.42278 | 0 | 335.707 | 330.407 | 5.2998 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:43 | 0515215-RetlMed-SG-HPWtrHtrSplitTnkCprsrOut | 0515215-srOut | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:47 | FAIL | -78.21 | -- | -- | Successful (88 warnings) | 0 | 103423 | 106143 | 0 | 0 | 3940.7 | 93480.7 | 306987 | 77659.3 | 0 | 424.545 | 0 | 385071 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 100.217 | 0 | 0 | 3.4089 | 93.0919 | 335.914 | 77.5842 | 0 | 0.42278 | 0 | 413.921 | 413.499 | 0.42212 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 554.362 | 0 | 840.937 | 0 | 0 | 0 | 0 | 840.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2723 | 93.0919 | 257.7 | 77.5842 | 0 | 0.42278 | 0 | 335.707 | 330.407 | 5.2998 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:44 | 0515315-RetlMed-SG-HPWtrHtrSplitTnkOutCprsrIns | 0515315-srInd | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -76.86 | -- | -- | Successful (94 warnings) | 0 | 101918 | 106136 | 0 | 0 | 3946.33 | 93480.7 | 305482 | 77659.3 | 0 | 424.545 | 0 | 383566 | 84.032 | 0 | 0 | 0 | 0 | 0 | 0 | 84.032 | 0 | 0 | 0 | 0 | 84.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5609 | 137.079 | 100.236 | 0 | 0 | 3.589 | 93.0919 | 334.557 | 77.5842 | 0 | 0.42278 | 0 | 412.564 | 412.003 | 0.5609 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 554.362 | 0 | 840.937 | 0 | 0 | 0 | 0 | 840.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2723 | 93.0919 | 257.7 | 77.5842 | 0 | 0.42278 | 0 | 335.707 | 330.407 | 5.2998 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:45 | 0515415-RetlMed-SG-UEFConsumerStoGas | 0515415-toGas | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -78.08 | -- | -- | Successful (83 warnings) | 0 | 103423 | 105858 | 0 | 0 | 0 | 93480.7 | 302762 | 77659.3 | 0 | 424.545 | 0 | 380846 | 64.7005 | 0 | 0 | 0 | 0 | 605.329 | 0 | 670.029 | 0 | 0 | 0 | 0 | 670.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 99.9842 | 0 | 0 | 3.569 | 93.0919 | 335.841 | 77.5842 | 0 | 0.42278 | 0 | 413.848 | 409.857 | 3.9911 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 562.213 | 0 | 848.787 | 0 | 0 | 0 | 0 | 848.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.3183 | 93.0919 | 257.746 | 77.5842 | 0 | 0.42278 | 0 | 335.753 | 330.407 | 5.3457 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:45 | 0515515-RetlMed-SG-UEFConsumerInstGas | 0515515-stGas | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -76.83 | -- | -- | Successful (83 warnings) | 0 | 103423 | 105858 | 0 | 0 | 0 | 93480.7 | 302762 | 77659.3 | 0 | 424.545 | 0 | 380846 | 64.7005 | 0 | 0 | 0 | 0 | 451.013 | 0 | 515.714 | 0 | 0 | 0 | 0 | 515.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 99.9842 | 0 | 0 | 2.6651 | 93.0919 | 334.937 | 77.5842 | 0 | 0.42278 | 0 | 412.944 | 409.857 | 3.0872 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 622.588 | 0 | 909.163 | 0 | 0 | 0 | 0 | 909.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.6716 | 93.0919 | 258.099 | 77.5842 | 0 | 0.42278 | 0 | 336.106 | 330.407 | 5.699 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:46 | 0515615-RetlMed-SG-UEFConsumerStoElec | 0515615-oElec | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -85.18 | -- | -- | Successful (83 warnings) | 0 | 103423 | 105858 | 0 | 0 | 11772.7 | 93480.7 | 314535 | 77659.3 | 0 | 424.545 | 0 | 392618 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 99.9842 | 0 | 0 | 11.0912 | 93.0919 | 343.363 | 77.5842 | 0 | 0.42278 | 0 | 421.37 | 420.948 | 0.42212 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 634.862 | 0 | 921.436 | 0 | 0 | 0 | 0 | 921.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.7434 | 93.0919 | 258.171 | 77.5842 | 0 | 0.42278 | 0 | 336.178 | 330.407 | 5.7709 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:47 | 0515715-RetlMed-SG-UEFConsumerInstElec | 0515715-tElec | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -85.67 | -- | -- | Successful (83 warnings) | 0 | 103423 | 105858 | 0 | 0 | 12211.7 | 93480.7 | 314974 | 77659.3 | 0 | 424.545 | 0 | 393057 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 64.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42212 | 138.774 | 99.9842 | 0 | 0 | 11.5124 | 93.0919 | 343.784 | 77.5842 | 0 | 0.42278 | 0 | 421.791 | 421.369 | 0.42212 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 622.588 | 0 | 909.163 | 0 | 0 | 0 | 0 | 909.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.6716 | 93.0919 | 258.099 | 77.5842 | 0 | 0.42278 | 0 | 336.106 | 330.407 | 5.699 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:48 | 0516015-RetlMed-SG-ExtWall-MtlFrmR0 | 0516015-FrmR0 | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -77.59 | -- | -- | Successful (83 warnings) | 0 | 103426 | 105858 | 0 | 0 | 0 | 93480.7 | 302764 | 77659.3 | 0 | 424.545 | 0 | 380848 | 64.7267 | 0 | 0 | 0 | 0 | 504.09 | 0 | 568.817 | 0 | 0 | 0 | 0 | 568.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42232 | 138.776 | 99.9842 | 0 | 0 | 2.9765 | 93.0919 | 335.25 | 77.5842 | 0 | 0.42278 | 0 | 413.257 | 409.859 | 3.3988 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 547.347 | 0 | 833.922 | 0 | 0 | 0 | 0 | 833.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2313 | 93.0919 | 257.659 | 77.5842 | 0 | 0.42278 | 0 | 335.666 | 330.407 | 5.2587 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:49 | 0516115-RetlMed-SG-ExtWall-WdFrmR0 | 0516115-FrmR0 | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -77.51 | -- | -- | Successful (83 warnings) | 0 | 103373 | 105858 | 0 | 0 | 0 | 93480.7 | 302711 | 77659.3 | 0 | 424.545 | 0 | 380795 | 64.2947 | 0 | 0 | 0 | 0 | 504.09 | 0 | 568.385 | 0 | 0 | 0 | 0 | 568.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41925 | 138.697 | 99.9842 | 0 | 0 | 2.9765 | 93.0919 | 335.168 | 77.5842 | 0 | 0.42278 | 0 | 413.175 | 409.78 | 3.3957 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 547.347 | 0 | 833.922 | 0 | 0 | 0 | 0 | 833.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2313 | 93.0919 | 257.659 | 77.5842 | 0 | 0.42278 | 0 | 335.666 | 330.407 | 5.2587 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:50 | 0516215-RetlMed-SG-ExtWall-MtlWallSingleLyrBatt-R10 | 0516215-t-R10 | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -75.82 | -- | -- | Successful (83 warnings) | 0 | 102275 | 105857 | 0 | 0 | 0 | 93480.7 | 301613 | 77659.3 | 0 | 424.545 | 0 | 379697 | 56.9675 | 0 | 0 | 0 | 0 | 504.09 | 0 | 561.057 | 0 | 0 | 0 | 0 | 561.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3675 | 137.064 | 99.9837 | 0 | 0 | 2.9765 | 93.0919 | 333.483 | 77.5842 | 0 | 0.42278 | 0 | 411.49 | 408.146 | 3.344 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 547.347 | 0 | 833.922 | 0 | 0 | 0 | 0 | 833.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2313 | 93.0919 | 257.659 | 77.5842 | 0 | 0.42278 | 0 | 335.666 | 330.407 | 5.2587 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:50 | 0516315-RetlMed-SG-ExtWall-MtlWallDoubleLyrBatt-R13-R13 | 0516315-3-R13 | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -74.3 | -- | -- | Successful (83 warnings) | 0 | 101280 | 105857 | 0 | 0 | 0 | 93480.7 | 300618 | 77659.3 | 0 | 424.545 | 0 | 378702 | 51.2344 | 0 | 0 | 0 | 0 | 504.089 | 0 | 555.324 | 0 | 0 | 0 | 0 | 555.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32749 | 135.584 | 99.9837 | 0 | 0 | 2.9765 | 93.0919 | 331.964 | 77.5842 | 0 | 0.42278 | 0 | 409.971 | 406.667 | 3.304 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6404 | 106057 | 19443.1 | 0 | 532.708 | 0 | 93480.7 | 219515 | 77659.3 | 0 | 424.545 | 0 | 297599 | 286.575 | 0 | 0 | 0 | 0 | 547.347 | 0 | 833.922 | 0 | 0 | 0 | 0 | 833.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0286 | 138.499 | 20.4331 | 0 | 0.37529 | 3.2313 | 93.0919 | 257.659 | 77.5842 | 0 | 0.42278 | 0 | 335.666 | 330.407 | 5.2587 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:51 | 0517015-RetlMed-SG-MiniSplitAC-EER11.2 | 0517015-R11.2 | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:45 | FAIL | -73.34 | -- | -- | Successful (81 warnings) | 25.2808 | 104248 | 95785.5 | 0 | 0 | 0 | 93480.7 | 293539 | 77659.3 | 0 | 424.545 | 0 | 371623 | 110.158 | 0 | 0 | 0 | 0 | 504.09 | 0 | 614.248 | 0 | 0 | 0 | 0 | 614.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78429 | 138.449 | 91.178 | 0 | 0 | 2.9765 | 93.0919 | 326.48 | 77.5842 | 0 | 0.42278 | 0 | 404.487 | 400.743 | 3.7432 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6872 | 102855 | 19409.1 | 0 | 640.731 | 0 | 93480.7 | 216387 | 77659.3 | 0 | 424.545 | 0 | 294471 | 299.36 | 0 | 0 | 0 | 0 | 547.347 | 0 | 846.707 | 0 | 0 | 0 | 0 | 846.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1151 | 133.909 | 20.3365 | 0 | 0.45055 | 3.2313 | 93.0919 | 253.135 | 77.5842 | 0 | 0.42278 | 0 | 331.142 | 325.796 | 5.3451 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\
| 2017-09-26 20:52 | 0517115-RetlMed-SG-MiniSplitHP-COP3.3 | 0517115-OP3.3 | PALM-SPRINGS-INTL_722868 | 24563.1 | 24692.3 | Title24Compliance | 0:46 | FAIL | -74.27 | -- | -- | Successful (83 warnings) | 11.9885 | 104682 | 96145.8 | 0 | 0 | 0 | 93480.7 | 294321 | 77659.3 | 0 | 424.545 | 0 | 372405 | 110.162 | 0 | 0 | 0 | 0 | 504.09 | 0 | 614.252 | 0 | 0 | 0 | 0 | 614.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77506 | 138.966 | 91.5855 | 0 | 0 | 2.9765 | 93.0919 | 327.395 | 77.5842 | 0 | 0.42278 | 0 | 405.402 | 401.659 | 3.7432 | 0 | 0 |  | 0 | 0 |  | 0 | -- | -- | Successful (77 warnings) | 1.6872 | 102855 | 19409.1 | 0 | 640.731 | 0 | 93480.7 | 216387 | 77659.3 | 0 | 424.545 | 0 | 294471 | 299.36 | 0 | 0 | 0 | 0 | 547.347 | 0 | 846.707 | 0 | 0 | 0 | 0 | 846.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1151 | 133.909 | 20.3365 | 0 | 0.45055 | 3.2313 | 93.0919 | 253.135 | 77.5842 | 0 | 0.42278 | 0 | 331.142 | 325.796 | 5.3451 | 0 | 0 |  | 0 | 0 |  | 0 | [26 empty] | CBECC-Com 2016.3.0 (963) | BEMCmpMgr 2016.3.0 (5160) | CA 2016 Nonresidential, Vers. 2.0 | 1.11.3.f52686d8e1 | 8.5 | - | D:\Public\Documents\CBECC-Com 2016.3.0 Data\EPW\ | D:\Public\Documents\CBECC-Com 2016.3.0 Projects\BatchOut_170926_v3-SST_SG\

## Sheet3 (hidden)
Small Office Building (02000CZ-OffSml) | Medium Office Building ((0300CZ-OffMed)) | Large Office Building (0400CZ-OffLrg) | Stand-alone Retail (0500CZ-RetlMed) | Strip Mall-PSZ System (1000CZ-RetlStrp)
5500 | 53627.8 | 498589 | 24563.1 | 22500
(90.8 ft x 60.5ft) | (163.8 ft x 109.2 ft) | (240 ft x 160 ft) | (178 ft x 139 ft) | (300 ft x 75 ft)