## Examples
Input cell | [7 empty] | << To add more spaces, insert copied columns before this column
1.15 | Story:ExhVentRatLimit
Sum
Maximum
Example 1)
Description: | CoreZn is indirectly conditioned/ventilated from PerimZn1
Comments: | Baseline rates equal proposed since proposed design total BuildingStory ventilation flow does not exceed the baseline total. Proportionality is maintained
| Notes |  | Gets transfer air from PerimZn1 | [5 empty] | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 0
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Baseline Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 1
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 10 | 10 | 10 | 10 | 10
| People | # | 16.109 | 12.212 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 1 | 1 | 1 | 1 | 1
| Prop Ra Flow | cfm | 96.654 | 73.272 | 43.464 | 73.272 | 43.464 |  | 330.126 | 330.126
| Prop Rp Flow | cfm | 80.545 | 61.06 | 36.22 | 61.06 | 36.22 |  | 275.105 | 275.105
| Prop Total Flow (P-Vbz) | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Prop Min Flow | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
CODE | Code Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 1 | 1 | 1 | 1 | 1
| Code Ra Flow | cfm | 96.654 | 73.272 | 43.464 | 73.272 | 43.464 |  | 330.126 | 330.126
| Code Rp Flow | cfm | 80.545 | 61.06 | 36.22 | 61.06 | 36.22 |  | 275.105 | 275.105
| Code Total Flow (B-Vbz) | cfm | 177.199 | 134.332 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Code Min Flow | cfm | 177.199 | 134.332 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 0 | 2.3191 | 1 | 1 | 1 |  |  |  |  | 1 | 1
| Exhaust Flow | cfm | 200 | 0 | 0 | 0 | 0 |  | 200 | 200 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0 | 0 | 0 | 0 | 0 |  |  | 0.33045 | 0 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Difference from P-Vbz | cfm | 0 | 0 | 0 | 0 | 0 |  | 0
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Prop VentPerAreaSim |  | 0 | 0.2551 | 0.11 | 0.11 | 0.11 |  | 605.231 | 605.231 | 0
| Prop VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base System OA Flow (B-Vot) | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Base VentPerAreaSim |  | 0 | 0.2551 | 0.11 | 0.11 | 0.11 |  | 605.231 | 605.231 | 0
| Base VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| CHECK |  | 0 | 311.531 | 79.684 | 134.332 | 79.684
Example 2)
Description: | Same as 1) but proposed is uniformly increased by: |  |  | 1.3
Comments: | Baseline rates equal to proposed * ratio to proporitionally reduce so total baseline BuildingStory ventilation air flow is equal to code design min.
| Notes | [7 empty] | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 0
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Baseline Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 1
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 10 | 10 | 10 | 10 | 10
| People | # | 16.109 | 12.212 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 1 | 1 | 1 | 1 | 1
| Prop Ra Flow | cfm | 96.654 | 73.272 | 43.464 | 73.272 | 43.464 |  | 330.126 | 330.126
| Prop Rp Flow | cfm | 80.545 | 61.06 | 36.22 | 61.06 | 36.22 |  | 275.105 | 275.105
| Prop Total Flow (P-Vbz) | cfm | 0 | 404.9903 | 103.5892 | 174.6316 | 103.5892 |  | 786.8003 | 786.8003 | 0
| Prop Min Flow | cfm | 0 | 404.9903 | 103.5892 | 174.6316 | 103.5892 |  | 786.8003 | 786.8003 | 0
CODE | Code Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 1 | 1 | 1 | 1 | 1
| Code Ra Flow | cfm | 96.654 | 73.272 | 43.464 | 73.272 | 43.464 |  | 330.126 | 330.126
| Code Rp Flow | cfm | 80.545 | 61.06 | 36.22 | 61.06 | 36.22 |  | 275.105 | 275.105
| Code Total Flow (B-Vbz) | cfm | 177.199 | 134.332 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Code Min Flow | cfm | 177.199 | 134.332 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 0 | 3.0148 | 1.3 | 1.3 | 1.3 |  |  |  |  | 0.76923 | 1
| Exhaust Flow | cfm | 200 | 0 | 0 | 0 | 0 |  | 200 | 200 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0 | 0 | 0 | 0 | 0 |  |  | 0.33045 | 0 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Difference from P-Vbz | cfm | 0 | 93.4593 | 23.9052 | 40.2996 | 23.9052 |  | 181.5693
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 0 | 404.9903 | 103.5892 | 174.6316 | 103.5892 |  | 786.8003 | 786.8003 | 0
| Prop VentPerAreaSim |  | 0 | 0.33163 | 0.143 | 0.143 | 0.143 |  | 786.8003 | 786.8003 | 0
| Prop VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base System OA Flow (B-Vot) | cfm | 0 | 311.531 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Base VentPerAreaSim |  | 0 | 0.2551 | 0.11 | 0.11 | 0.11 |  | 605.231 | 605.231 | 0
| Base VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| CHECK |  | 0 | 311.531 | 79.684 | 134.332 | 79.684
Example 3)
Description: | Same as example 1 but add extra 50cfm to PerimZn1 and CoreZn has a an exhaust fan
Comments: | Baseline rates equal to proposed * multiplier to proporitionally reduce proposed rates so total baseline BuildingStory ventilation air flow is equal to code design min.
| Notes |  | Gets transfer air from PerimZn1, has 200cfm of general exhaust | Includes vent for CoreZn + 50cfm |  |  |  |  | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 0
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Baseline Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 1
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 10 | 10 | 10 | 10 | 10
| People | # | 16.109 | 12.212 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 1 | 1 | 1 | 1 | 1
| Prop Ra Flow | cfm | 96.654 | 73.272 | 43.464 | 73.272 | 43.464 |  | 330.126 | 330.126
| Prop Rp Flow | cfm | 80.545 | 61.06 | 36.22 | 61.06 | 36.22 |  | 275.105 | 275.105
| Prop Total Flow (P-Vbz) | cfm | 0 | 361.531 | 79.684 | 134.332 | 79.684 |  | 655.231 | 655.231 | 0
| Prop Min Flow | cfm | 0 | 361.531 | 79.684 | 134.332 | 79.684 |  | 655.231 | 655.231 | 0
CODE | Code Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 1 | 1 | 1 | 1 | 1
| Code Ra Flow | cfm | 96.654 | 73.272 | 43.464 | 73.272 | 43.464 |  | 330.126 | 330.126
| Code Rp Flow | cfm | 80.545 | 61.06 | 36.22 | 61.06 | 36.22 |  | 275.105 | 275.105
| Code Total Flow (B-Vbz) | cfm | 177.199 | 134.332 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0
| Code Min Flow | cfm | 177.199 | 134.332 | 79.684 | 134.332 | 79.684 |  | 605.231 | 605.231 | 0 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 0 | 2.6913 | 1 | 1 | 1 |  |  |  |  | 0.92369 | 1
| Exhaust Flow | cfm | 200 | 0 | 0 | 0 | 0 |  | 200 | 200 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0 | 0 | 0 | 0 | 0 |  |  | 0.33045 | 0 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 0 | 333.9429 | 73.6034 | 124.0813 | 73.6034 |  | 605.231 | 605.231 | 0
| Difference from P-Vbz | cfm | 0 | 27.5881 | 6.0806 | 10.2507 | 6.0806 |  | 50
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 0 | 361.531 | 79.684 | 134.332 | 79.684 |  | 655.231 | 655.231 | 0
| Prop VentPerAreaSim |  | 0 | 0.29605 | 0.11 | 0.11 | 0.11 |  | 655.231 | 655.231 | 0
| Prop VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base System OA Flow (B-Vot) | cfm | 0 | 333.9429 | 73.6034 | 124.0813 | 73.6034 |  | 605.231 | 605.231 | 0
| Base VentPerAreaSim |  | 0 | 0.27345 | 0.10161 | 0.10161 | 0.10161 |  | 605.231 | 605.231 | 0
| Base VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| CHECK |  | 0 | 333.9429 | 73.6034 | 124.0813 | 73.6034
Example 4)
Description: | CoreZn is a commercial kitchen with exhaust, and make-up air is provided to PerimZn1. Ez = 0.8 for all zones
Comments: | Baseline rates is greater than code, but limited to 1.1x BuildingStory exhaust air flow.
| Notes |  | Commercial kitchen w/ exhaust | Provided extra ventilation for kitchen make-up (i.e. dining area) |  |  |  |  | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 0
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Baseline Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 1
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 5 | 5 | 10 | 10 | 10
| People | # | 8.0545 | 6.106 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.12 | 0.12 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 7.5 | 7.5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Prop Ra Flow | cfm | 241.635 | 183.18 | 54.33 | 91.59 | 54.33 |  | 625.065 | 625.065
| Prop Rp Flow | cfm | 75.5109 | 57.2437 | 45.275 | 76.325 | 45.275 |  | 299.6297 | 299.6297
| Prop Total Flow (P-Vbz) | cfm | 317.1459 | 600 | 99.605 | 167.915 | 99.605 |  | 1284.2709 | 1284.2709 | 0
| Prop Min Flow | cfm | 317.1459 | 600 | 99.605 | 167.915 | 99.605 |  | 1284.2709 | 1284.2709 | 0
CODE | Code Ra | cfm/sf | 0.12 | 0.12 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 7.5 | 7.5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Code Ra Flow | cfm | 241.635 | 183.18 | 54.33 | 91.59 | 54.33 |  | 625.065 | 625.065
| Code Rp Flow | cfm | 75.5109 | 57.2437 | 45.275 | 76.325 | 45.275 |  | 299.6297 | 299.6297
| Code Total Flow (B-Vbz) | cfm | 317.1459 | 240.4238 | 99.605 | 167.915 | 99.605 |  | 924.6947 | 924.6947 | 0
| Code Min Flow | cfm | 317.1459 | 240.4238 | 99.605 | 167.915 | 99.605 |  | 924.6947 | 924.6947 | 0 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 1 | 2.4956 | 1 | 1 | 1 |  |  |  |  | 0.72002 | 1
| Exhaust Flow | cfm | 1000 | 0 | 0 | 0 | 0 |  | 1000 | 1000 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0.31715 | 0 | 0 | 0 | 0 |  |  | 1.0814 | 0 | 1.2437 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 283.9882 | 537.2698 | 89.1913 | 150.3594 | 89.1913 |  | 1150 | 1150 | 0 | Exhaust exception applies, ventilation up to 115% of exhaust flow allowed
| Difference from P-Vbz | cfm | 33.1577 | 62.7302 | 10.4137 | 17.5556 | 10.4137 |  | 134.2709 |  |  | CHECK: 1.15
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 317.1459 | 600 | 99.605 | 167.915 | 99.605 |  | 1284.2709 | 1284.2709 | 0
| Prop VentPerAreaSim |  | 0.19687 | 0.49132 | 0.1375 | 0.1375 | 0.1375 |  | 1284.2709 | 1284.2709 | 0
| Prop VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base System OA Flow (B-Vot) | cfm | 283.9882 | 537.2698 | 89.1913 | 150.3594 | 89.1913 |  | 1150 | 1150 | 0
| Base VentPerAreaSim |  | 0.17629 | 0.43995 | 0.12312 | 0.12312 | 0.12312 |  | 1150 | 1150 | 0
| Base VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| CHECK |  | 283.9882 | 537.2698 | 89.1913 | 150.3594 | 89.1913
Example 4b)
Description: | Space 2 is a commercial kitchen with exhaust, and make-up air is provided to dining area (Space 1)
Comments: | Baseline rates equal to proposed since total proposed BuildingStory ventilation air flow is less than 1.1x BuildingStory exhaust air flow. Adjustments made to constant/person components individually.
| Notes |  | Dining room | Comm. kitchen w/ exhaust |  |  |  |  | BuildingStory
| Space Name |  | Space 1 | Space 2 | Space 3 | Space 4 | Space 5 |  | Sum of All Spaces | Sum of Incl. Spaces |  | Adjustments
| Include? |  | 1 | 1 | 1 | 1 | 1
| Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Is Lab Space? |  | 0 | 0 | 0 | 0 | 0
| Prop Ra Flow | cfm | 400 | 100 | 50 | 150 | 50 |  | 750 | 750
| Prop Rp Flow | cfm | 150 | 100 | 50 | 150 | 50 |  | 500 | 500
| Proposed Total Design | cfm | 550 | 200 | 100 | 300 | 100 |  | 1250 | 1250
| Code Ra Flow | cfm | 50 | 100 | 50 | 150 | 50 |  | 400 | 400
| Code Rp Flow | cfm | 50 | 100 | 50 | 150 | 50 |  | 400 | 400
| Code Min Design Total | cfm | 100 | 200 | 100 | 300 | 100 |  | 800 | 800
| Ratio Prop:Code Vent, Ra |  | 8 | 1 | 1 | 1 | 1 |  |  |  |  | 0.53333 | Story:MinVentPerAreaRat
| Ratio Prop:Code Vent, Rp |  | 3 | 1 | 1 | 1 | 1 |  |  |  |  | 0.8 | Story:MinVentPerPersonRat
| Ratio Prop:Code Vent Total |  | 5.5 | 1 | 1 | 1 | 1 |  |  |  |  | 0.64 | Story:MinVentBalRat
| Exhaust | cfm | 0 | 1000 | 0 | 0 | 0 |  | 1000 | 1000
| Ratio Vent:Exh |  | 0 | 0.2 | 0 | 0 | 0 |  |  |  |  | 1.4375 | Story:ExhVentMult
| Baseline Simulated Design Total | cfm | 479.1667 | 191.6667 | 95.8333 | 287.5 | 95.8333 |  | 1150 | 1150 |  | Exhaust exception applies, ventilation up to 115% of exhaust flow allowed
| Difference from Proposed | cfm | 70.8333 | 8.3333 | 4.1667 | 12.5 | 4.1667 |  | 100
| Baseline VentPerAreaSim |  | 479.1667 | 191.6667 | 95.8333 | 287.5 | 95.8333 |  | 1150
| Baseline VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 |  | 0
Example 5)
Description: | CoreZn uses VentStd = 'Other' and is over-ventilated
Comments: | Based on user input of CodeOther values, the baseline flow is adjusted down to match code Min.
| Notes |  | VentStd = 'Other', Has DCV |  |  |  | VentStd = 'Other', Has DCV |  | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 1 | 0 | 0 | 0 | 1
| Specification Method |  | Sum | Sum | Sum | Sum | Maximum
| Proposed Has DCV? |  | 1 | 0 | 0 | 0 | 1
| Baseline Has DCV? |  | 1 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 0 | 1 | 1 | 1 | 0
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 41 | 10 | 10 | 10 | 10
| People | # | 66.0469 | 12.212 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.1 | 0.06 | 0.06 | 0.06 | 0.16667
| Prop Rp | cfm/per | 6 | 5 | 5 | 5 | 25
| Prop Zone Vent Eff (P-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Prop Ra Flow | cfm | 201.3625 | 91.59 | 54.33 | 91.59 | 150.9167 |  | 589.7892 | 237.51
| Prop Rp Flow | cfm | 495.3518 | 76.325 | 45.275 | 76.325 | 226.375 |  | 919.6518 | 197.925
| Prop Total Flow (P-Vbz) | cfm | 696.7143 | 167.915 | 99.605 | 167.915 | 226.375 |  | 1358.5243 | 435.435 | 923.0893
| Prop Min Flow | cfm | 201.3625 | 167.915 | 99.605 | 167.915 | 150.9167 |  | 787.7142 | 435.435 | 352.2792
CODE | Code Ra | cfm/sf | 0.08 | 0.06 | 0.06 | 0.06 | 0.16667
| Code Rp | cfm/per | 5 | 5 | 5 | 5 | 20
| Base Zone Vent Eff (B-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Code Ra Flow | cfm | 161.09 | 91.59 | 54.33 | 91.59 | 150.9167 |  | 549.5167 | 237.51
| Code Rp Flow | cfm | 412.7931 | 76.325 | 45.275 | 76.325 | 181.1 |  | 791.8181 | 197.925
| Code Total Flow (B-Vbz) | cfm | 573.8831 | 167.915 | 99.605 | 167.915 | 181.1 |  | 1190.4181 | 435.435 | 754.9831
| Code Min Flow | cfm | 161.09 | 167.915 | 99.605 | 167.915 | 181.1 |  | 777.625 | 435.435 | 342.19 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 1.214 | 1 | 1 | 1 | 1.25 |  |  |  |  | 1 | 0.81789
| Exhaust Flow | cfm | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 569.8339 | 167.915 | 99.605 | 167.915 | 185.1493 |  | 1190.4181 | 435.435 | 754.9831
| Difference from P-Vbz | cfm | 126.8804 | 0 | 0 | 0 | 41.2257 |  | 168.1061
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 696.7143 | 167.915 | 99.605 | 167.915 | 226.375 |  | 1358.5243 | 435.435 | 923.0893
| Prop VentPerAreaSim |  | 0.125 | 0.1375 | 0.1375 | 0.1375 | 0.20833 |  | 787.7142 | 435.435 | 352.2792
| Prop VentPerPersonSim |  | 7.5 | 0 | 0 | 0 | 31.25 | 0 | 620 | 0 | 620
| Base System OA Flow (B-Vot) | cfm | 569.8339 | 167.915 | 99.605 | 167.915 | 185.1493 |  | 1190.4181 | 435.435 | 754.9831
| Base VentPerAreaSim |  | 0.1 | 0.1375 | 0.1375 | 0.1375 | 0.25559 |  | 781.6743 | 435.435 | 346.2393
| Base VentPerPersonSim |  | 6.1887 | 0 | 0 | 0 | 0 |  | 253.7363 | 0 | 253.7363
| CHECK |  | 569.8339 | 167.915 | 99.605 | 167.915 | 185.1493
Example 6)
Description: | CoreZn space has DCV and elevated Rp
Comments: | Baseline Ra is specified at code minimum, with balance simulated as Rp flow
| Notes |  | Space has DCV and elevated Rp | [5 empty] | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 0
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 1 | 0 | 0 | 0 | 0
| Baseline Has DCV? |  | 1 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 1
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 66.67 | 10 | 10 | 10 | 10
| People | # | 107.3987 | 12.212 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.18 | 0.06 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 10 | 5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Prop Ra Flow | cfm | 362.4525 | 91.59 | 54.33 | 91.59 | 54.33 |  | 654.2925 | 654.2925
| Prop Rp Flow | cfm | 1342.4838 | 76.325 | 45.275 | 76.325 | 45.275 |  | 1585.6838 | 1585.6838
| Prop Total Flow (P-Vbz) | cfm | 1704.9363 | 167.915 | 99.605 | 167.915 | 99.605 |  | 2239.9763 | 2239.9763 | 0
| Prop Min Flow | cfm | 362.4525 | 167.915 | 99.605 | 167.915 | 99.605 |  | 897.4925 | 897.4925 | 0
CODE | Code Ra | cfm/sf | 0.18 | 0.06 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 7.5 | 5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Code Ra Flow | cfm | 362.4525 | 91.59 | 54.33 | 91.59 | 54.33 |  | 654.2925 | 654.2925
| Code Rp Flow | cfm | 1006.8628 | 76.325 | 45.275 | 76.325 | 45.275 |  | 1250.0628 | 1250.0628
| Code Total Flow (B-Vbz) | cfm | 1369.3153 | 167.915 | 99.605 | 167.915 | 99.605 |  | 1904.3553 | 1904.3553 | 0
| Code Min Flow | cfm | 362.4525 | 167.915 | 99.605 | 167.915 | 99.605 |  | 897.4925 | 897.4925 | 0 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 1.2451 | 1 | 1 | 1 | 1 |  |  |  |  | 0.85017 | 1
| Exhaust Flow | cfm | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 1449.4816 | 142.7559 | 84.6809 | 142.7559 | 84.6809 |  | 1904.3553 | 1904.3553 | 0
| Difference from P-Vbz | cfm | 255.4546 | 25.1591 | 14.9241 | 25.1591 | 14.9241 |  | 335.6209
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 1704.9363 | 167.915 | 99.605 | 167.915 | 99.605 |  | 2239.9763 | 2239.9763 | 0
| Prop VentPerAreaSim |  | 0.225 | 0.1375 | 0.1375 | 0.1375 | 0.1375 |  | 897.4925 | 897.4925 | 0
| Prop VentPerPersonSim |  | 12.5 | 0 | 0 | 0 | 0 | 0 | 833.375 | 833.375 | 0
| Base System OA Flow (B-Vot) | cfm | 1449.4816 | 142.7559 | 84.6809 | 142.7559 | 84.6809 |  | 1904.3553 | 1904.3553 | 0
| Base VentPerAreaSim |  | 0.225 | 0.1169 | 0.1169 | 0.1169 | 0.1169 |  | 817.3262 | 817.3262 | 0
| Base VentPerPersonSim |  | 10.1214 | 0 | 0 | 0 | 0 |  | 674.7962 | 674.7962 | 0
| CHECK |  | 1449.4816 | 142.7559 | 84.6809 | 142.7559 | 84.6809
Example 7)
Description: | THE WHOLE ENCHILADA!!! Combination of all examples.
Comments:
| Notes |  | Commercial kitchen w/ exhaust | Provided extra ventilation for kitchen make-up (i.e. dining area) and has DCV | Gets transfer air from PerimZn3, has 200cfm of general exhaust | Includes vent for PerimZn2 + 50cfm | VentStd = 'Other' |  | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 1
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 0 | 1 | 0 | 0 | 0
| Baseline Has DCV? |  | 0 | 1 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 0
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 5 | 66.67 | 10 | 10 | 10
| People | # | 8.0545 | 81.4174 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.12 | 0.18 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 7.5 | 7.5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Prop Ra Flow | cfm | 241.635 | 274.77 | 54.33 | 91.59 | 54.33 |  | 716.655 | 662.325
| Prop Rp Flow | cfm | 75.5109 | 763.2882 | 45.275 | 76.325 | 45.275 |  | 1005.6741 | 960.3991
| Prop Total Flow (P-Vbz) | cfm | 317.1459 | 1038.0582 | 0 | 317.52 | 99.605 |  | 1772.3291 | 1672.7241 | 99.605
| Prop Min Flow | cfm | 317.1459 | 274.77 | 0 | 317.52 | 99.605 |  | 1009.0409 | 909.4359 | 99.605
CODE | Code Ra | cfm/sf | 0.12 | 0.18 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 7.5 | 7.5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Code Ra Flow | cfm | 241.635 | 274.77 | 54.33 | 91.59 | 54.33 |  | 716.655 | 662.325
| Code Rp Flow | cfm | 75.5109 | 763.2882 | 45.275 | 76.325 | 45.275 |  | 1005.6741 | 960.3991
| Code Total Flow (B-Vbz) | cfm | 317.1459 | 1038.0582 | 99.605 | 167.915 | 99.605 |  | 1722.3291 | 1622.7241 | 99.605
| Code Min Flow | cfm | 317.1459 | 274.77 | 99.605 | 167.915 | 99.605 |  | 959.0409 | 859.4359 | 99.605 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 1 | 1 | 0 | 1.891 | 1 |  |  |  |  | 0.97011 | 1
| Exhaust Flow | cfm | 600 | 0 | 200 | 0 | 100 |  | 900 | 800 | 100 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0.52858 | 0 | 0 | 0 | 0.99605 |  |  | 0.493 | 1.004 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 307.666 | 1007.0292 | 0 | 308.0289 | 99.605 |  | 1722.3291 | 1622.7241 | 99.605
| Difference from P-Vbz | cfm | 9.4799 | 31.029 | 0 | 9.4911 | 0 |  | 50
| Prop System Vent Eff (P-Ev) |  | 1 | 1 | 1 | 1 | 1
| Prop System OA Flow (P-Vot) | cfm | 317.1459 | 1038.0582 | 0 | 317.52 | 99.605 |  | 1772.3291 | 1672.7241 | 99.605
| Prop VentPerAreaSim |  | 0.19687 | 0.225 | 0 | 0.26001 | 0.1375 |  | 1009.0409 | 909.4359 | 99.605
| Prop VentPerPersonSim |  | 0 | 9.375 | 0 | 0 | 0 | 0 | 625.0312 | 625.0312 | 0
| Base System OA Flow (B-Vot) | cfm | 307.666 | 1007.0292 | 0 | 308.0289 | 99.605 |  | 1722.3291 | 1622.7241 | 99.605
| Base VentPerAreaSim |  | 0.19099 | 0.225 | 0 | 0.25223 | 0.1375 |  | 990.0699 | 890.4649 | 99.605
| Base VentPerPersonSim |  | 0 | 8.9939 | 0 | 0 | 0 |  | 599.6227 | 599.6227 | 0
| CHECK |  | 307.666 | 1007.0292 | 0 | 308.0289 | 99.605
Example 8)
Description: | Multi-zone
Comments: | Baseline rates equal proposed since proposed design total BuildingStory ventilation flow does not exceed the baseline total. Proportionality is maintained
| Notes |  | Gets transfer air from PerimZn1 | [5 empty] | BuildingStory
| Space Name |  | CoreZn | PerimZn1 | PerimZn2 | PerimZn3 | PerimZn4 |  | Sum of All Spaces | Sum of VentStd Spaces | Sum of Other Spaces | CodeAdjustment | CodeOtherAdjustment
| VentStd = "Other" |  | 0 | 0 | 0 | 0 | 0
| Specification Method |  | Sum | Sum | Sum | Sum | Sum
| Proposed Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Baseline Has DCV? |  | 0 | 0 | 0 | 0 | 0
| Uses VentStd? |  | 1 | 1 | 1 | 1 | 1
| Floor Area | ft2 | 1610.9 | 1221.2 | 724.4 | 1221.2 | 724.4
| Occupant Density | #/1000sf | 10 | 10 | 10 | 10 | 10
| People | # | 16.109 | 12.212 | 7.244 | 12.212 | 7.244
PROPOSED | Prop Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Prop Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Prop Zone Vent Eff (P-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Prop Ra Flow | cfm | 120.8175 | 91.59 | 54.33 | 91.59 | 54.33 |  | 412.6575 | 412.6575
| Prop Rp Flow | cfm | 100.6813 | 76.325 | 45.275 | 76.325 | 45.275 |  | 343.8813 | 343.8813
| Prop Total Flow (P-Vbz) | cfm | 0 | 389.4137 | 99.605 | 167.915 | 99.605 |  | 756.5387 | 756.5387 | 0
| Prop Min Flow | cfm | 0 | 389.4137 | 99.605 | 167.915 | 99.605 |  | 756.5387 | 756.5387 | 0
CODE | Code Ra | cfm/sf | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Code Rp | cfm/per | 5 | 5 | 5 | 5 | 5
| Base Zone Vent Eff (B-Ez) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Code Ra Flow | cfm | 120.8175 | 91.59 | 54.33 | 91.59 | 54.33 |  | 412.6575 | 412.6575
| Code Rp Flow | cfm | 100.6813 | 76.325 | 45.275 | 76.325 | 45.275 |  | 343.8813 | 343.8813
| Code Total Flow (B-Vbz) | cfm | 221.4988 | 167.915 | 99.605 | 167.915 | 99.605 |  | 756.5388 | 756.5388 | 0
| Code Min Flow | cfm | 221.4988 | 167.915 | 99.605 | 167.915 | 99.605 |  | 756.5388 | 756.5388 | 0 | Story:CodeVentMult | Story:CodeOtherVentMult
| Ratio Prop:Code, Total |  | 0 | 2.3191 | 1 | 1 | 1 |  |  |  |  | 1 | 1
| Exhaust Flow | cfm | 200 | 0 | 0 | 0 | 0 |  | 200 | 200 | 0 | Story:ExhVentMult | Story:ExhOtherVentMult
| Ratio Vent:Exh |  | 0 | 0 | 0 | 0 | 0 |  |  | 0.26436 | 0 | 1 | 1
| Base Total Flow (B-Vbz) TARGET | cfm | 0 | 389.4138 | 99.605 | 167.915 | 99.605 |  | 756.5388 | 756.5388 | 0
| Difference from P-Vbz | cfm | 0 | 0 | 0 | 0 | 0 |  | 0
| Prop System Vent Eff (P-Ev) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Prop System OA Flow (P-Vot) | cfm | 0 | 486.7672 | 124.5062 | 209.8938 | 124.5062 |  | 945.6734 | 945.6734 | 0
| Prop VentPerAreaSim |  | 0 | 0.3986 | 0.17187 | 0.17188 | 0.17187 |  | 945.6734 | 945.6734 | 0
| Prop VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base System OA Flow (B-Vot) | cfm | 0 | 486.7672 | 124.5063 | 209.8938 | 124.5063 |  | 945.6734 | 945.6734 | 0
| Base VentPerAreaSim |  | 0 | 0.3986 | 0.17188 | 0.17188 | 0.17188 |  | 945.6734 | 945.6734 | 0
| Base VentPerPersonSim |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| CHECK |  | 0 | 486.7672 | 124.5063 | 209.8938 | 124.5063
Note on K12: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B42: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B45: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K55: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B85: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B88: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K98: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B128: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B131: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K141: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B171: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B174: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K183: David Reddy: Included spaces are all spaces except process spaces (lab and commercial kitchen) and spaces with DCV.
Note on K209: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B239: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B242: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K252: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B282: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B285: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K295: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B325: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B328: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on K338: David Reddy: Included spaces are all spaces except spaces defined to have: 1) Cross-pressurization/contamination requirements 2) Use DCV controls 3) Utilze VentStd = 'Other'
Note on B368: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.
Note on B371: David Reddy: As distributed to zone in DesignSpecification:OutdoorAir objects.

## Property Outline
|  | Proposed | Baseline
Controls | ThrmlZn | VentSpecMthd |  |  | Properties echod at Space
VentSpecMthdSim
VentCtrlMthd
Component Inputs | Space | VentPerArea | CodeVentPerArea | CodeOtherVentPerArea
|  | VentPerPerson | CodeVentPerPerson | CodeOtherVentPerPerson
|  | VentACH |  | CodeOtherVentACH
Component Flows | Space | VentPerAreaFlow | CodeVentPerAreaFlow
|  | VentPerPersonFlow | CodeVentPerPersonFlow
|  | VentACHFlow | CodeVentACHFlow
Design Flow | Space | VentFlow | CodeVentFlow | CodeOtherVentFlow
Design Minimum Flow | Space | MinVentFlow | CodeMinVentFlow | CodeOtherMinVentFlow
Flow for Balance Calcs | Space | VentFlowForBal | CodeVentFlowForBal
|  | MinVentFlowForBal | CodeMinVentFlowForBal
Multipliers | Story |  | CodeVentMult | CodeOtherVentMult
|  |  | ExhVentMult | OtherExhVentMult
| Space |  | CodeVentMult
ExhVentMult
| Space |  | CodeVentFlowTarget
VentPerAreaFlowSim
VentPerPersonFlowSim
CodeVentPerPersonFlowSim

## Sheet1
Questions
| 360 | PNNL
X | If VentStd = 'Other', and the proposed design has DCV, does the baseline have DCV as well? I suggest that the baseline rules for determining the use of DCV remain as they normally would, and only the ventilation/exhaust rates are maintained the same between the two designs. This is because there will be times when the zone may not exceed the occ density requirement, or, the baseline system may not meet the prerequisites specified in 6.4.3.9. | [SG] I agree with your approach. The ventilation/exhaust rates can be same as proposed and rules for DCV are applied if applicable
| Up to this point, I've been assuming that we would calculate Vot for systems within rules based on user inputs, and then for simulation, specify DesignSpecification:OutdoorAir objects for each zone which specify OA flows including adjustments for Ez and Ev. However, I recall we discussed using E+'s internal ability to calculate ventilation rates using Controller:MechanicalVentilation -> System Outdoor Air Method = VentilationRateProcedure. Please confirm that PNNL is not assuming we use E+'s implementation of VRP. Instead, I am proposing we will use the current method, ZoneSum, and the SDD inputs for DesignSpecification:OutdoorAir will include the effectiveness adjustments made in rules. | [SG] Yes, we had decided to not use E+’s capability for implementing the VRP. The OA rates calculated would be entered under DSOA object. However, there is a limitation is OS at present which prevents a correct implementation of this approach. I will send you a separate email regarding that.
| For Ez, do we need to allow input of both a heating and cooling zone effectiveness? I've been assuming the user would only input one value, and that would be the smaller of heating/cooling effectiveness. | [SG] I don’t see how will be able to use both so smaller of the two works fine. Roger/Mike- please feel free to weigh in if this approach doesn’t sound correct.
If user specifys just an OA for zone CFM, how should the program allocate the OA to cfm_minimum vs cfm_person if DCV is used?
In the Story ventilation balance calculations, I assume I should use the design ventilation rate, not the cfm_minimum in determining the amount of ventilation air to baseline allowance?