## Sheet1
;
TABLE T24N_2022FanPwrIdxAdj
; |  |  | Exhaust systems required by code to be fully ducted | Return systems required by code to be fully ducted | Exhaust filters, scrubbers, or other exhaust treatment (calculation required, see note) | Particulate filtration credit: MERV 16 or greater and electronically enhanced filters | Carbon and other gas-phase air cleaners (calculation required, see note) | Biosafety cabinet (calculation required, see note) | Energy Recovery (Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | Single Zone VAV Systems that are capable of turning down to 50% of full load airflow at a maximum of 30% design wattage
| SysType | FlowCap | FullyDuctedExh | FullyDuctedRet | ExhFilters | MERVGTE16 | GasPhaseAirCleaners | BiosftyCabExh | ERV | SZVAV
| MultiZoneVAV | <=5000 | 0.089 | 0.089 | 0.177 | 0.265 | 0.176 | 0.177 | 0.374 | 0
| MultiZoneVAV | <=10000 | 0.1 | 0.1 | 0.198 | 0.28 | 0.188 | 0.198 | 0.318 | 0
| MultiZoneVAV | >10000 | 0.116 | 0.116 | 0.231 | 0.333 | 0.224 | 0.231 | 0.289 | 0
| AllOther | <=5000 | 0.091 | 0.091 | 0.179 | 0.264 | 0.177 | 0.179 | 0.381 | 0.07
| AllOther | <=10000 | 0.102 | 0.102 | 0.202 | 0.292 | 0.197 | 0.202 | 0.329 | 0.1
| AllOther | >10000 | 0.116 | 0.116 | 0.232 | 0.342 | 0.231 | 0.232 | 0.293 | 0.089
ENDTABLE
;
TABLE T24N_2022BaseFanPwrIdx
; |  |  | 1 – SZAC (with furnace) | 3 – PSZ-HP (no furnace) | 3 – PSZ-AC (with furnace) | 5 – PVAV with reheat | 6 – VAV with reheat | 7 – SZ VAV (no furnace) | 7 – SZ VAV (with furnace) | 9 – Heating and Ventilation
|  | FlowCap | Sys1 | Sys4 | Sys3 | Sys5 | Sys6 | Sys7h | Sys7a | Sys9
|  | <=5000 | 0.756 | 0.744 | 0.802 | 1 | 0.977 | 0.744 | 0.802 | 0.616
|  | <=10000 | 0.74 | 0.72 | 0.78 | 1.022 | 1.013 | 0.72 | 0.78 | 0.62
|  | >10000 | 0.712 | 0.676 | 0.748 | 0.964 | 0.947 | 0.676 | 0.748 | 0.605
ENDTABLE