## Fan Static Pressure Adj_Backup (hidden)
Key:
Input Values
Intermediate Values
Check Values
Error
Tolerrance: | 1%
| PROPOSED | [27 empty] | Paste ap - FanPowerAdjustment -> | AirSystems
| Air Systems | [30 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
| System Name | Type | SupFanCap | RetFanCap | ReliefFanCap | ExhFanCap | SupFanPwr | RetFanPwr | ReliefFanPwr | ExhFanPwr | TotSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio |  |  | TotSysFanPwrAdj | ExhFiltersPDAdj | BiosftyCabPDAdj | FullyDuctedRetPDAdj | MERVGTE16PDAdj | GasPhaseAirCleanersPDAdj | ExhFiltersDevFlow | BiosftyCabDevFlow | FullyDuctedRetDevFlow | MERVGTE16DevFlow | GasPhaseAirCleanersDevFlow |  | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj | Exhaust Filter Pressure Drop Adj | Biosafety Cabinet Pressure Drop Adj | Fully Ducted Return Pressure Drop Adj | MERV16 Filter Pressure Drop Adj | Air Cleaner Pressure Drop Adj | Exhaust Filter Designed Flow | Biosafety Designed Flow | Fully Ducted Return Designed Flow | MERV16 Filter Designed Flow | Air Cleaner Designed Flow
|  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | [16 empty] | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
| BottomVAV | PVAV | 17875.9 | 0 | 16982.1 | 0 | 15.789 | 0 | 4.352 | 0 | 20.141 | 0.784 | 0 | 0.216 | 0 |  |  | 7.2482 | 0 | 0 | 0.5 | 1.2 | 0 | 0 | 0 | 16982 | 17876 | 0 |  | BottomVAV | PVAV | 17875.9 | 0 | 16982.1 | 0 | 15.789 | 0 | 4.352 | 0 | 20.141 | 0.784 | 0 | 0.216 | 0 | 0 | 7.259 | 7.259 | 0 | 0 | 0.5 | 1.2 | 0 | 0 | 0 | 16982 | 17876 | 0
| Mid VAV-SW Zones | PVAV | 3644.6 | 2962.3 | 0 | 0 | 3.345 | 1.006 | 0 | 0 | 4.351 | 0.769 | 0.231 | 0 | 0 |  |  | 1.0588 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 3645 | 0 |  | Mid VAV-SW Zones | PVAV | 3644.6 | 2962.3 | 0 | 0 | 3.345 | 1.006 | 0 | 0 | 4.351 | 0.769 | 0.231 | 0 | 0 | 0 | 1.06 | 1.06 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 3645 | 0
| Mid VAV NE_Core Zones | PVAV | 14231.4 | 0 | 13119.8 | 0 | 12.57 | 0 | 3.445 | 0 | 16.015 | 0.785 | 0 | 0.215 | 0 |  |  | 4.1339 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 14231 |  | Mid VAV NE_Core Zones | PVAV | 14231.4 | 0 | 13119.8 | 0 | 12.57 | 0 | 3.445 | 0 | 16.015 | 0.785 | 0 | 0.215 | 0 | 0 | 4.14 | 4.14 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 14231
| Mid SE Zones ExhSys | Exhaust | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0.825 | 0.825 | 0 | 0 | 0 | 1 |  |  | 0.22876 | 0.5 | 1.1 | 0 | 0 | 0 | 900 | 450 | 0 | 0 | 0 |  | Mid SE Zones ExhSys | Exhaust | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0.825 | 0.825 | 0 | 0 | 0 | 1 | 0.229 | 0 | 0 | 0.5 | 1.1 | 0 | 0 | 0 | 900 | 450 | 0 | 0 | 0
| TopFlrDOAS | DOASCV | 1565 | 0 | 0 | 0 | 1.486 | 0 | 0 | 0 | 1.486 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | TopFlrDOAS | DOASCV | 1565 | 0 | 0 | 0 | 1.486 | 0 | 0 | 0 | 1.486 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Top SW Zones ExhSys | Exhaust | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0.366 | 0.366 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Top SW Zones ExhSys | Exhaust | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0.366 | 0.366 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ZoneSystems
| Zone Systems | [30 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
| System Name | Type | SupFanCap | RetFanCap | ReliefFanCap | ExhFanCap | SupFanPwr | RetFanPwr | ReliefFanPwr | ExhFanPwr | TotSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio |  |  | TotSysFanPwrAdj | ExhFiltersPDAdj | BiosftyCabPDAdj | FullyDuctedRetPDAdj | MERVGTE16PDAdj | GasPhaseAirCleanersPDAdj | ExhFiltersDevFlow | BiosftyCabDevFlow | FullyDuctedRetDevFlow | MERVGTE16DevFlow | GasPhaseAirCleanersDevFlow |  | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj | Exhaust Filter Pressure Drop Adj | Biosafety Cabinet Pressure Drop Adj | Fully Ducted Return Pressure Drop Adj | MERV16 Filter Pressure Drop Adj | Air Cleaner Pressure Drop Adj | Exhaust Filter Designed Flow | Biosafety Designed Flow | Fully Ducted Return Designed Flow | MERV16 Filter Designed Flow | Air Cleaner Designed Flow
|  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | [16 empty] | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
| Perim_TopZn1_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn1_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perim_TopZn2_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn2_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perim_TopZn3_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn3_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perim_TopZn4_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn4_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Core_TopZn_PTAC | PTAC | 3000 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 1.05 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Core_TopZn_PTAC | PTAC | 3000 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 1.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thermal Zone
[36 empty] | Fan Capacity |  |  | Fan Flow Ratio |  |  | Fan Pwr |  |  |  |  | Fan Pwr Adj
| Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | PriAirCondgSysDsgnFlow | VentSysDsgnFlow | DsgnExhFlow | PriZnToSysAirFlowRatio | VentZnToSysAirFlowRatio | ExhZnToSysAirFlowRatio | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | TotExhFanPwrAdj | TotNonExhFanPwrAdj | TotFanPwrAdj | ExhFiltersFanPwrAdj | BiosftyCabFanPwrAdj | FullyDuctedRetFanPwrAdj | MERVGTE16FanPwrAdj | GasPhaseAirCleanersFanPwrAdj | [6 empty] | Name | Pri. HVAC Sys. | Vent. Sys. | Exhaust Sys. | Floor Area | Multiplier | Pri. System Flow | Ventilation System Flow | Exhaust Flow | Zn. Pri. Air Flow to Sys. Air Flow Ratio | Zn. Vent. to Sys. Air Flow Ratio | Zn. Exhaust to Sys. Air Flow Ratio | Prop. Supply Fan Pwr. | Prop. Return Fan Pwr. | Prop. Relief Fan Pwr. | Prop. Exhaust Fan Pwr. | Total Prop. Fan Pwr | Total Exhaust Fan Pwr. Adj | Total NonExhaust Fan Pwr. Adj | Total Fan Pwr. Adj | Exhaust Filter Fan Pwr Adj | Biosafety Cabinet Fan Pwr Adj | Fully Ducted Return Fan Pwr Adj | MERV16 Fan Pwr Adj | Air Cleaner Fan Pwr Adj
[5 empty] | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | [10 empty] | (ft2) |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
| Core_bottom Thermal Zone | BottomVAV | BottomVAV | NONE | 10586.7 | 10586.7 | 0 | 0.59223 | 0 | 0 | 9.3508 | 0 | 2.5774 | 0 | 11.9282 | 0 | 4.2926 | 4.2926 | 0 | 0 | 1.2173 | 3.0753 | 0 | [6 empty] | Core_bottom Thermal Zone | BottomVAV | BottomVAV | NONE | 10586.7 | 1 | 10586.7 | 10586.7 | 0 | 0.592 | 0 | 0 | 9.351 | 0 | 2.577 | 0 | 11.928 | 0 | 4.299 | 4.299 | 0 | 0 | 1.219 | 3.08 | 0
| Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 2231.8 | 0 | 0.12485 | 0 | 0 | 1.9713 | 0 | 0.54335 | 0 | 2.5146 | 0 | 0.90493 | 0.90493 | 0 | 0 | 0.25662 | 0.64831 | 0 | [6 empty] | Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.906 | 0.906 | 0 | 0 | 0.257 | 0.649 | 0
| Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.9 | 1412.9 | 0 | 0.079039 | 0 | 0 | 1.248 | 0 | 0.34398 | 0 | 1.5919 | 0 | 0.57289 | 0.57289 | 0 | 0 | 0.16246 | 0.41043 | 0 | [6 empty] | Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.9 | 1 | 1412.9 | 1412.9 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.574 | 0.574 | 0 | 0 | 0.163 | 0.411 | 0
| Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 2231.8 | 0 | 0.12485 | 0 | 0 | 1.9713 | 0 | 0.54335 | 0 | 2.5146 | 0 | 0.90493 | 0.90493 | 0 | 0 | 0.25662 | 0.64831 | 0 | [6 empty] | Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.906 | 0.906 | 0 | 0 | 0.257 | 0.649 | 0
| Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.8 | 1412.8 | 0 | 0.079034 | 0 | 0 | 1.2479 | 0 | 0.34396 | 0 | 1.5918 | 0 | 0.57285 | 0.57285 | 0 | 0 | 0.16245 | 0.4104 | 0 | [6 empty] | Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.8 | 1 | 1412.8 | 1412.8 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.574 | 0.574 | 0 | 0 | 0.163 | 0.411 | 0
| FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 10586.7 | 10586.7 | 0 | 0.7439 | 0 | 0 | 9.3508 | 0 | 2.5627 | 0 | 11.9135 | 0 | 3.0752 | 3.0752 | 0 | 0 | 0 | 0 | 3.0752 | [6 empty] | Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 10586.7 | 1 | 10586.7 | 10586.7 | 0 | 0.744 | 0 | 0 | 9.351 | 0 | 2.563 | 0 | 11.913 | 0 | 3.08 | 3.08 | 0 | 0 | 0 | 0 | 3.08
| Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.8 | 2231.8 | 500 | 0.61236 | 0 | 0.55556 | 2.0483 | 0.61603 | 0 | 0.45833 | 3.1227 | 0.12709 | 0.64838 | 0.77547 | 0.060518 | 0.06657 | 0 | 0.64838 | 0 | [6 empty] | Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.8 | 1 | 2231.8 | 2231.8 | 500 | 0.612 | 0 | 0.556 | 2.048 | 0.616 | 0 | 0.458 | 3.122 | 0.127 | 0.649 | 0.777 | 0.061 | 0.067 | 0 | 0.649 | 0
| Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | 1412.9 | 1412.9 | 400 | 0.09928 | 0 | 0.44444 | 1.248 | 0 | 0.34202 | 0.36667 | 1.9566 | 0.10167 | 0.41042 | 0.51209 | 0.048414 | 0.053256 | 0 | 0 | 0.41042 | [6 empty] | Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | 1412.9 | 1 | 1412.9 | 1412.9 | 400 | 0.099 | 0 | 0.444 | 1.248 | 0 | 0.342 | 0.366 | 1.956 | 0.102 | 0.411 | 0.513 | 0.048 | 0.053 | 0 | 0 | 0.411
| Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 2231.8 | 2231.8 | 0 | 0.15682 | 0 | 0 | 1.9713 | 0 | 0.54025 | 0 | 2.5115 | 0 | 0.64829 | 0.64829 | 0 | 0 | 0 | 0 | 0.64829 | [6 empty] | Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.157 | 0 | 0 | 1.971 | 0 | 0.54 | 0 | 2.511 | 0 | 0.649 | 0.649 | 0 | 0 | 0 | 0 | 0.649
| Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | NONE | 1412.8 | 1412.8 | 0 | 0.38764 | 0 | 0 | 1.2967 | 0.38997 | 0 | 0 | 1.6866 | 0 | 0.41044 | 0.41044 | 0 | 0 | 0 | 0.41044 | 0 | [6 empty] | Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | NONE | 1412.8 | 1 | 1412.8 | 1412.8 | 0 | 0.388 | 0 | 0 | 1.297 | 0.39 | 0 | 0 | 1.687 | 0 | 0.411 | 0.411 | 0 | 0 | 0 | 0.411 | 0
| MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS | NONE | 3000 | 1165 | 0 | 1 | 0.74441 | 0 | 2.1562 | 0 | 0 | 0 | 2.1562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS | NONE | 10586.7 | 1 | 3000 | 1165 | 0 | 1 | 0.744 | 0 | 2.156 | 0 | 0 | 0 | 2.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Perim_TopZn1_PTAC | Top SW Zones ExhSys | 2000 | 2000 | 245 | 1 | 0 | 0.6125 | 0.7 | 0 | 0 | 0.22418 | 0.92417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Perim_TopZn1_PTAC | Top SW Zones ExhSys | 2231.8 | 1 | 2000 | 2000 | 245 | 1 | 0 | 0.613 | 0.7 | 0 | 0 | 0.224 | 0.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | Perim_TopZn2_PTAC | Top SW Zones ExhSys | 2000 | 2000 | 155 | 1 | 0 | 0.3875 | 0.7 | 0 | 0 | 0.14183 | 0.84182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | Perim_TopZn2_PTAC | Top SW Zones ExhSys | 1412.9 | 1 | 2000 | 2000 | 155 | 1 | 0 | 0.388 | 0.7 | 0 | 0 | 0.142 | 0.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS | NONE | 2000 | 245 | 0 | 1 | 0.15655 | 0 | 0.93263 | 0 | 0 | 0 | 0.93263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS | NONE | 2231.8 | 1 | 2000 | 245 | 0 | 1 | 0.157 | 0 | 0.933 | 0 | 0 | 0 | 0.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS | NONE | 2000 | 155 | 0 | 1 | 0.099042 | 0 | 0.84718 | 0 | 0 | 0 | 0.84718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS | NONE | 1412.8 | 1 | 2000 | 155 | 0 | 1 | 0.099 | 0 | 0.847 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BASELINE | [27 empty] | Paste ab - FanPowerAdjustment -> | AirSystems
[32 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
| System Name | Type | TotPropSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | TotExhSysFanPwrAdj | TotNonExhSysFanPwrAdj | TotSysFanPwrAdj | [19 empty] | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj | Exhaust Filter Pressure Drop Adj | Biosafety Cabinet Pressure Drop Adj | Fully Ducted Return Pressure Drop Adj | MERV16 Filter Pressure Drop Adj | Air Cleaner Pressure Drop Adj | Exhaust Filter Designed Flow | Biosafety Designed Flow | Fully Ducted Return Designed Flow | MERV16 Filter Designed Flow | Air Cleaner Designed Flow
|  |  | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (BHP) | (BHP) | (BHP) | [21 empty] | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
| BaseAirSys5 |  | 20.1411 | 0.78392 | 0 | 0.21608 | 0 | 0 | 5.7677 | 5.7677 | [19 empty] | BaseAirSys5 | PVAV | 14224.8 | 0 | 0 | 0 | 17.195 | 0 | 3.5 | 0 | 20.141 | 0.784 | 0 | 0.216 | 0 | 0 | 5.777 | 5.777 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996
| BaseAirSys5-2 |  | 21.191 | 0.75103 | 0.047473 | 0.16257 | 0.038932 | 0.22876 | 4.1442 | 4.373 | [19 empty] | BaseAirSys5-2 | PVAV | 14266.4 | 0 | 0 | 0 | 15.928 | 0 | 3.275 | 0 | 21.19 | 0.751 | 0.047 | 0.163 | 0.039 | 0.229 | 4.151 | 4.151 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996
| BaseAirSys5-3 |  | 5.702 | 0.93581 | 0 | 0 | 0.064188 | 0 | 0 | 0 | [19 empty] | BaseAirSys5-3 | PVAV | 14697.7 | 0 | 0 | 0 | 12.982 | 0 | 3.519 | 0 | 5.703 | 0.936 | 0 | 0 | 0.064 | 0 | 0 | 0 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996
Thermal Zone
[36 empty] | Fan Capacity |  |  | Fan Flow Ratio |  |  | Fan Pwr |  |  |  |  | Fan Pwr Adj
| Thermal Zone | PriAirCondgSysRef | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | PriAirCondgSysDsgnFlow | BaseToPropDsgnFlowRat | [6 empty] | TotExhFanPwrAdj | TotNonExhFanPwrAdj | TotFanPwrAdj | ExhFiltersFanPwrAdj | BiosftyCabFanPwrAdj | FullyDuctedRetFanPwrAdj | MERVGTE16FanPwrAdj | GasPhaseAirCleanersFanPwrAdj | [6 empty] | Name | Pri. HVAC Sys. | Vent. Sys. | Exhaust Sys. | Floor Area | Multiplier | Pri. System Flow | Ventilation System Flow | Exhaust Flow | Zn. Pri. Air Flow to Sys. Air Flow Ratio | Zn. Vent. to Sys. Air Flow Ratio | Zn. Exhaust to Sys. Air Flow Ratio | Prop. Supply Fan Pwr. | Prop. Return Fan Pwr. | Prop. Relief Fan Pwr. | Prop. Exhaust Fan Pwr. | Total Prop. Fan Pwr | Total Exhaust Fan Pwr. Adj | Total NonExhaust Fan Pwr. Adj | Total Fan Pwr. Adj | Exhaust Filter Fan Pwr Adj | Biosafety Cabinet Fan Pwr Adj | Fully Ducted Return Fan Pwr Adj | MERV16 Fan Pwr Adj | Air Cleaner Fan Pwr Adj
|  |  | (kW) | (kW) | (kW) | (kW) | (kW) | (cfm) | (frac) | [6 empty] | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | [10 empty] | (ft2) |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
| Core_bottom Thermal Zone | BaseAirSys5 | 9.3508 | 0 | 2.5774 | 0 | 11.9282 | 7965.5 | 0.75241 | [6 empty] | 0 | 3.2298 | 3.2298 | 0 | 0 | 0.9159 | 2.3139 | 0 | [6 empty] | Core_bottom Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 10586.7 | 1 | 7965.5 | 7965.5 | 0 | 0.592 | 0 | 0 | 9.351 | 0 | 2.577 | 0 | 11.928 | 0 | 3.235 | 3.235 | 0 | 0 | 0.917 | 2.317 | 0
| Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys5 | 1.9713 | 0 | 0.54335 | 0 | 2.5146 | 2068 | 0.92661 | [6 empty] | 0 | 0.83852 | 0.83852 | 0 | 0 | 0.23779 | 0.60073 | 0 | [6 empty] | Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 2231.8 | 1 | 2068 | 2068 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.84 | 0.84 | 0 | 0 | 0.238 | 0.602 | 0
| Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys5 | 1.248 | 0 | 0.34398 | 0 | 1.5919 | 1330.9 | 0.94196 | [6 empty] | 0 | 0.53964 | 0.53964 | 0 | 0 | 0.15303 | 0.38661 | 0 | [6 empty] | Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 1412.9 | 1 | 1330.9 | 1330.9 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.54 | 0.54 | 0 | 0 | 0.153 | 0.387 | 0
| Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys5 | 1.9713 | 0 | 0.54335 | 0 | 2.5146 | 1431.7 | 0.6415 | [6 empty] | 0 | 0.58051 | 0.58051 | 0 | 0 | 0.16462 | 0.41589 | 0 | [6 empty] | Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 2231.8 | 1 | 1431.7 | 1431.7 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.581 | 0.581 | 0 | 0 | 0.165 | 0.417 | 0
| Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys5 | 1.2479 | 0 | 0.34396 | 0 | 1.5918 | 1428.6 | 1.0112 | [6 empty] | 0 | 0.57926 | 0.57926 | 0 | 0 | 0.16427 | 0.41499 | 0 | [6 empty] | Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 1412.8 | 1 | 1428.6 | 1428.6 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.58 | 0.58 | 0 | 0 | 0.165 | 0.416 | 0
| FirstFloor_Plenum Thermal Zone | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Core_mid Thermal Zone | BaseAirSys5-2 | 9.3508 | 0 | 2.5627 | 0 | 11.9135 | 7360.4 | 0.69525 | [6 empty] | 0 | 2.138 | 2.138 | 0 | 0 | 0 | 0 | 2.138 | [6 empty] | Core_mid Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 10586.7 | 1 | 7360.4 | 7360.4 | 0 | 0.744 | 0 | 0 | 9.351 | 0 | 2.563 | 0 | 11.913 | 0 | 2.141 | 2.141 | 0 | 0 | 0 | 0 | 2.141
| Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys5-2 | 2.0483 | 0.61603 | 0 | 0.45833 | 3.1227 | 2373.9 | 1.0637 | [6 empty] | 0.12709 | 0.68966 | 0.81675 | 0.060518 | 0.06657 | 0 | 0.68966 | 0 | [6 empty] | Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 2231.8 | 1 | 2373.9 | 2373.9 | 500 | 0.612 | 0 | 0.556 | 2.048 | 0.616 | 0 | 0.458 | 3.122 | 0.127 | 0.691 | 0.818 | 0.061 | 0.067 | 0 | 0.691 | 0
| Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys5-2 | 1.248 | 0 | 0.34202 | 0.36667 | 1.9566 | 1492 | 1.056 | [6 empty] | 0.10167 | 0.43339 | 0.53506 | 0.048414 | 0.053256 | 0 | 0 | 0.43339 | [6 empty] | Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 1412.9 | 1 | 1492 | 1492 | 400 | 0.099 | 0 | 0.444 | 1.248 | 0 | 0.342 | 0.366 | 1.956 | 0.102 | 0.434 | 0.536 | 0.048 | 0.053 | 0 | 0 | 0.434
| Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys5-2 | 1.9713 | 0 | 0.54025 | 0 | 2.5115 | 1415.9 | 0.63442 | [6 empty] | 0 | 0.41129 | 0.41129 | 0 | 0 | 0 | 0 | 0.41129 | [6 empty] | Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 2231.8 | 1 | 1415.9 | 1415.9 | 0 | 0.157 | 0 | 0 | 1.971 | 0 | 0.54 | 0 | 2.511 | 0 | 0.412 | 0.412 | 0 | 0 | 0 | 0 | 0.412
| Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys5-2 | 1.2967 | 0.38997 | 0 | 0 | 1.6866 | 1624.1 | 1.1496 | [6 empty] | 0 | 0.47183 | 0.47183 | 0 | 0 | 0 | 0.47183 | 0 | [6 empty] | Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 1412.8 | 1 | 1624.1 | 1624.1 | 0 | 0.388 | 0 | 0 | 1.297 | 0.39 | 0 | 0 | 1.687 | 0 | 0.473 | 0.473 | 0 | 0 | 0 | 0.473 | 0
| MidFloor_Plenum Thermal Zone | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Core_top Thermal Zone | BaseAirSys5-3 | 2.1562 | 0 | 0 | 0 | 2.1562 | 7618.8 | 2.5396 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Core_top Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 10586.7 | 1 | 7618.8 | 7618.8 | 0 | 1 | 0.744 | 0 | 2.156 | 0 | 0 | 0 | 2.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_1 Thermal Zone | BaseAirSys5-3 | 0.7 | 0 | 0 | 0.22418 | 0.92417 | 2411.7 | 1.2058 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_1 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 2231.8 | 1 | 2411.7 | 2411.7 | 245 | 1 | 0 | 0.613 | 0.7 | 0 | 0 | 0.224 | 0.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_2 Thermal Zone | BaseAirSys5-3 | 0.7 | 0 | 0 | 0.14183 | 0.84182 | 1474.9 | 0.73745 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_2 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 1412.9 | 1 | 1474.9 | 1474.9 | 155 | 1 | 0 | 0.388 | 0.7 | 0 | 0 | 0.142 | 0.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_3 Thermal Zone | BaseAirSys5-3 | 0.93263 | 0 | 0 | 0 | 0.93263 | 1496.7 | 0.74835 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_3 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 2231.8 | 1 | 1496.7 | 1496.7 | 0 | 1 | 0.157 | 0 | 0.933 | 0 | 0 | 0 | 0.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perimeter_top_ZN_4 Thermal Zone | BaseAirSys5-3 | 0.84718 | 0 | 0 | 0 | 0.84718 | 1695.5 | 0.84775 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Perimeter_top_ZN_4 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 1412.8 | 1 | 1695.5 | 1695.5 | 0 | 1 | 0.099 | 0 | 0.847 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TopFloor_Plenum Thermal Zone | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Fan Power Ratios - SP_Backup (hidden)
Key:
Input Values
Intermediate Values
Check Values
PROPOSED
[7 empty] | 1 | [8 empty] | 3.445 | [6 empty] | AirSystems
|  |  |  | Flows |  |  | Ratios |  |  | Zone Fan Pwrs | [14 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | PriAirCondgSysDsgnFlow | VentSysDsgnFlow | DsgnExhFlow | PriZnToSysFlowRat | VentZnToSysFlowRat | ExhZnToSysAirFlowRatio | PriSysPropSupFanPwr | VentSysPropSupFanPwr | TotPropSupFanPwr | PriSysPropRetFanPwr | VentSysPropRetFanPwr | TotPropRetFanPwr | PriSysPropReliefFanPwr | VentSysPropReliefFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPriSysPropFanPwr | TotVentSysPropFanPwr | TotPropFanPwr | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj
|  |  |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW)
Core_bottom Thermal Zone | BottomVAV | BottomVAV |  | 10586.7 | 10586.7 | 0 | 0.59223 | - | - | 9.3508 | - | 9.3508 | 0 | - | 0 | 2.5774 | - | 2.5774 | - | 11.9282 | - | 11.9282 | BottomVAV | PVAV | 17875.9 | 0 | 16982.1 | 0 | 15.789 | 0 | 4.352 | 0 | 20.141 | 0.784 | 0 | 0.216 | 0 | 0 | 7.259 | 7.259
Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV |  | 2231.8 | 2231.8 | 0 | 0.12485 | - | - | 1.9713 | - | 1.9713 | 0 | - | 0 | 0.54335 | - | 0.54335 | - | 2.5146 | - | 2.5146 | Mid VAV-SW Zones | PVAV | 3644.6 | 2962.3 | 0 | 0 | 3.345 | 1.006 | 0 | 0 | 4.351 | 0.769 | 0.231 | 0 | 0 | 0 | 1.06 | 1.06
Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV |  | 1412.9 | 1412.9 | 0 | 0.079039 | - | - | 1.248 | - | 1.248 | 0 | - | 0 | 0.34398 | - | 0.34398 | - | 1.5919 | - | 1.5919 | Mid VAV NE_Core Zones | PVAV | 14231.4 | 0 | 13119.8 | 0 | 12.57 | 0 | 3.445 | 0 | 16.015 | 0.785 | 0 | 0.215 | 0 | 0 | 4.14 | 4.14
Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV |  | 2231.8 | 2231.8 | 0 | 0.12485 | - | - | 1.9713 | - | 1.9713 | 0 | - | 0 | 0.54335 | - | 0.54335 | - | 2.5146 | - | 2.5146 | Mid SE Zones ExhSys | Exhaust | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0.825 | 0.825 | 0 | 0 | 0 | 1 | 0.229 | 0 | 0
Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV |  | 1412.8 | 1412.8 | 0 | 0.079034 | - | - | 1.2479 | - | 1.2479 | 0 | - | 0 | 0.34396 | - | 0.34396 | - | 1.5918 | - | 1.5918 | TopFlrDOAS | DOASCV | 1565 | 0 | 0 | 0 | 1.486 | 0 | 0 | 0 | 1.486 | 1 | 0 | 0 | 0 | 0 | 0 | 0
FirstFloor_Plenum Thermal Zone | NONE | NONE |  | 0 | 0 | 0 | [16 empty] | Top SW Zones ExhSys | Exhaust | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0.366 | 0.366 | 0 | 0 | 0 | 1 | 0 | 0 | 0
Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones |  | 10586.7 | 10586.7 | 0 | 0.7439 | - | - | 9.3508 | - | 9.3508 | 0 | - | 0 | 2.5627 | - | 2.5627 | - | 11.9135 | - | 11.9135
Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.8 | 2231.8 | 500 | 0.61236 | - | 0.55556 | 2.0483 | - | 2.0483 | 0.61603 | - | 0.61603 | 0 | - | 0 | 0.45833 | 2.6644 | - | 3.1227 | ZoneSystems
Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | 1412.9 | 1412.9 | 400 | 0.09928 | - | 0.44444 | 1.248 | - | 1.248 | 0 | - | 0 | 0.34202 | - | 0.34202 | 0.36667 | 1.59 | - | 1.9566 |  |  | Fan Capacity |  |  |  | Fan Pwr (Design) | [5 empty] | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones |  | 2231.8 | 2231.8 | 0 | 0.15682 | - | - | 1.9713 | - | 1.9713 | 0 | - | 0 | 0.54025 | - | 0.54025 | - | 2.5115 | - | 2.5115 | Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Total Fan Pwr | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Total Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total Fan Pwr Adj
Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones |  | 1412.8 | 1412.8 | 0 | 0.38764 | - | - | 1.2967 | - | 1.2967 | 0.38997 | - | 0.38997 | 0 | - | 0 | - | 1.6866 | - | 1.6866 |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW)
MidFloor_Plenum Thermal Zone | NONE | NONE |  | 0 | 0 | 0 | [16 empty] | Perim_TopZn1_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS |  | 3000 | 1165 | 0 | 1 | 0.74441 | - | 1.05 | 1.1062 | 2.1562 | 0 | 0 | 0 | 0 | 0 | 0 | - | 1.05 | 1.1062 | 2.1562 | Perim_TopZn2_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Perim_TopZn1_PTAC | Top SW Zones ExhSys | 2000 | 2000 | 245 | 1 | - | 0.6125 | 0.7 | - | 0.7 | 0 | - | 0 | 0 | - | 0 | 0.22418 | 0.7 | - | 0.92417 | Perim_TopZn3_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | Perim_TopZn2_PTAC | Top SW Zones ExhSys | 2000 | 2000 | 155 | 1 | - | 0.3875 | 0.7 | - | 0.7 | 0 | - | 0 | 0 | - | 0 | 0.14183 | 0.7 | - | 0.84182 | Perim_TopZn4_PTAC | PTAC | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS |  | 2000 | 245 | 0 | 1 | 0.15655 | - | 0.7 | 0.23263 | 0.93263 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0.7 | 0.23263 | 0.93263 | Core_TopZn_PTAC | PTAC | 3000 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 1.05 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS |  | 2000 | 155 | 0 | 1 | 0.099042 | - | 0.7 | 0.14718 | 0.84718 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0.7 | 0.14718 | 0.84718
TopFloor_Plenum Thermal Zone | NONE | NONE |  | 0 | 0 | 0 | [16 empty] | Thermal Zone
[29 empty] | Fan Capacity |  |  | Fan Flow Ratio |  |  | Fan Pwr |  |  |  |  | Fan Pwr Adj
[23 empty] | Name | Pri. HVAC Sys. | Vent. Sys. | Exhaust Sys. | Floor Area | Multiplier | Pri. System Flow | Ventilation System Flow | Exhaust Flow | Zn. Pri. Air Flow to Sys. Air Flow Ratio | Zn. Vent. to Sys. Air Flow Ratio | Zn. Exhaust to Sys. Air Flow Ratio | Prop. Supply Fan Pwr. | Prop. Return Fan Pwr. | Prop. Relief Fan Pwr. | Prop. Exhaust Fan Pwr. | Total Prop. Fan Pwr | Total Exhaust Fan Pwr. Adj | Total NonExhaust Fan Pwr. Adj | Total Fan Pwr. Adj
[27 empty] | (ft2) |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW)
Systems |  |  |  | SupFanCap | RetFanCap | ReliefFanCap | ExhFlow | SupFanPwr | RetFanPwr | ReliefFanPwr | ExhFanPwr | TotPropSysFanPwr | TotPropSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | [5 empty] | Core_bottom Thermal Zone | BottomVAV | BottomVAV | NONE | 10586.7 | 1 | 10586.7 | 10586.7 | 0 | 0.592 | 0 | 0 | 9.351 | 0 | 2.577 | 0 | 11.928 | 0 | 4.299 | 4.299
|  |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | [5 empty] | Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.906 | 0.906
BottomVAV | PVAV |  |  | 17875.9 | 0 | 16982.1 | 0 | 15.789 | 0 | 4.352 | 0 | 20.141 | 20.1411 | 0.78392 | 0 | 0.21608 | 0 | [5 empty] | Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.9 | 1 | 1412.9 | 1412.9 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.574 | 0.574
Mid VAV-SW Zones | PVAV |  |  | 3644.6 | 2962.3 | 0 | 0 | 3.345 | 1.006 | 0 | 0 | 4.351 | 4.351 | 0.76879 | 0.23121 | 0 | 0 | [5 empty] | Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.906 | 0.906
Mid VAV NE_Core Zones | PVAV |  |  | 14231.4 | 0 | 13119.8 | 0 | 12.57 | 0 | 3.445 | 0 | 16.015 | 16.015 | 0.78489 | 0 | 0.21511 | 0 | [5 empty] | Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.8 | 1 | 1412.8 | 1412.8 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.574 | 0.574
Mid SE Zones ExhSys | Exhaust |  |  | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0.825 | 0.825 | 0.825 | 0 | 0 | 0 | 1 | [5 empty] | FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TopFlrDOAS | SZAC |  |  | 1565 | 0 | 0 | 0 | 1.486 | 0 | 0 | 0 | 1.486 | 1.486 | 1 | 0 | 0 | 0 | [5 empty] | Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 10586.7 | 1 | 10586.7 | 10586.7 | 0 | 0.744 | 0 | 0 | 9.351 | 0 | 2.563 | 0 | 11.913 | 0 | 3.08 | 3.08
Top SW Zones ExhSys | Exhaust |  |  | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0.366 | 0.366 | 0.366 | 0 | 0 | 0 | 1 | [5 empty] | Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.8 | 1 | 2231.8 | 2231.8 | 500 | 0.612 | 0 | 0.556 | 2.048 | 0.616 | 0 | 0.458 | 3.122 | 0.127 | 0.649 | 0.777
Perim_TopZn1_PTAC | PTAC |  |  | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 0.7 | 1 | 0 | 0 | 0 | [5 empty] | Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | 1412.9 | 1 | 1412.9 | 1412.9 | 400 | 0.099 | 0 | 0.444 | 1.248 | 0 | 0.342 | 0.366 | 1.956 | 0.102 | 0.411 | 0.513
Perim_TopZn2_PTAC | PTAC |  |  | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 0.7 | 1 | 0 | 0 | 0 | [5 empty] | Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.157 | 0 | 0 | 1.971 | 0 | 0.54 | 0 | 2.511 | 0 | 0.649 | 0.649
Perim_TopZn3_PTAC | PTAC |  |  | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 0.7 | 1 | 0 | 0 | 0 | [5 empty] | Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | NONE | 1412.8 | 1 | 1412.8 | 1412.8 | 0 | 0.388 | 0 | 0 | 1.297 | 0.39 | 0 | 0 | 1.687 | 0 | 0.411 | 0.411
Perim_TopZn4_PTAC | PTAC |  |  | 2000 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0.7 | 0.7 | 1 | 0 | 0 | 0 | [5 empty] | MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_TopZn_PTAC | PTAC |  |  | 3000 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0 | 1.05 | 1.05 | 1 | 0 | 0 | 0 | [5 empty] | Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS | NONE | 10586.7 | 1 | 3000 | 1165 | 0 | 1 | 0.744 | 0 | 2.156 | 0 | 0 | 0 | 2.156 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Perim_TopZn1_PTAC | Top SW Zones ExhSys | 2231.8 | 1 | 2000 | 2000 | 245 | 1 | 0 | 0.613 | 0.7 | 0 | 0 | 0.224 | 0.924 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | Perim_TopZn2_PTAC | Top SW Zones ExhSys | 1412.9 | 1 | 2000 | 2000 | 155 | 1 | 0 | 0.388 | 0.7 | 0 | 0 | 0.142 | 0.842 | 0 | 0 | 0
BASELINE | [22 empty] | Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS | NONE | 2231.8 | 1 | 2000 | 245 | 0 | 1 | 0.157 | 0 | 0.933 | 0 | 0 | 0 | 0.933 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS | NONE | 1412.8 | 1 | 2000 | 155 | 0 | 1 | 0.099 | 0 | 0.847 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0
|  |  |  | Zone Fan Powers | [18 empty] | TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | ZnToSysExhFanPwrRatio | ExhFanMtrBHP
|  |  |  | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (bhp)
Core_bottom Thermal Zone | BaseAirSys5 |  |  | 9.3508 | 0 | 2.5774 | - | 11.9282 | - | -
Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys5 |  |  | 1.9713 | 0 | 0.54335 | - | 2.5146 | - | -
Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys5 |  |  | 1.248 | 0 | 0.34398 | - | 1.5919 | - | -
Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys5 |  |  | 1.9713 | 0 | 0.54335 | - | 2.5146 | - | -
Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys5 |  |  | 1.2479 | 0 | 0.34396 | - | 1.5918 | - | -
Core_mid Thermal Zone | BaseAirSys5-2 |  |  | 9.3508 | 0 | 2.5627 | - | 11.9135 | - | -
Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys5-2 |  |  | 2.0483 | 0.61603 | 0 | 0.45833 | 3.1227 | 0.55556 | 0.49571
Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys5-2 |  |  | 1.248 | 0 | 0.34202 | 0.36667 | 1.9566 | 0.44444 | 0.39657 | [12 empty] | AirSystems
Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys5-2 |  |  | 1.9713 | 0 | 0.54025 | - | 2.5115 | - | - | [14 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys5-2 |  |  | 1.2967 | 0.38997 | 0 | - | 1.6866 | - | - | [12 empty] | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj
Core_top Thermal Zone | BaseAirSys5-3 |  |  | 2.1562 | 0 | 0 | - | 2.1562 | - | - | [14 empty] | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW)
Perimeter_top_ZN_1 Thermal Zone | BaseAirSys5-3 |  |  | 0.7 | 0 | 0 | 0.22418 | 0.92417 | 0.6125 | 0.7512 | [12 empty] | BaseAirSys5 | PVAV | 14224.8 | 0 | 0 | 0 | 17.195 | 0 | 3.5 | 0 | 20.141 | 0.784 | 0 | 0.216 | 0 | 0 | 5.777 | 5.777
Perimeter_top_ZN_2 Thermal Zone | BaseAirSys5-3 |  |  | 0.7 | 0 | 0 | 0.14183 | 0.84182 | 0.3875 | 0.47525 | [12 empty] | BaseAirSys5-2 | PVAV | 14266.4 | 0 | 0 | 0 | 15.928 | 0 | 3.275 | 0 | 21.19 | 0.751 | 0.047 | 0.163 | 0.039 | 0.229 | 4.151 | 4.151
Perimeter_top_ZN_3 Thermal Zone | BaseAirSys5-3 |  |  | 0.93263 | 0 | 0 | - | 0.93263 | - | - | [12 empty] | BaseAirSys5-3 | PVAV | 14697.7 | 0 | 0 | 0 | 12.982 | 0 | 3.519 | 0 | 5.703 | 0.936 | 0 | 0 | 0.064 | 0 | 0 | 0
Perimeter_top_ZN_4 Thermal Zone | BaseAirSys5-3 |  |  | 0.84718 | 0 | 0 | - | 0.84718 | - | -
Thermal Zone
[29 empty] | Fan Capacity |  |  | Fan Flow Ratio |  |  | Fan Pwr |  |  |  |  | Fan Pwr Adj
[13 empty] | MtrBHP | [9 empty] | Name | Pri. HVAC Sys. | Vent. Sys. | Exhaust Sys. | Floor Area | Multiplier | Pri. System Flow | Ventilation System Flow | Exhaust Flow | Zn. Pri. Air Flow to Sys. Air Flow Ratio | Zn. Vent. to Sys. Air Flow Ratio | Zn. Exhaust to Sys. Air Flow Ratio | Prop. Supply Fan Pwr. | Prop. Return Fan Pwr. | Prop. Relief Fan Pwr. | Prop. Exhaust Fan Pwr. | Total Prop. Fan Pwr | Total Exhaust Fan Pwr. Adj | Total NonExhaust Fan Pwr. Adj | Total Fan Pwr. Adj
Systems |  |  |  | SupFanCap | TotPropSysFanPwr | PropExhFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | BaseFanBHPAllowance | BaseFanBHPWithPressDropCredit | Supply Fan | Return Fan | Relief Fan | Ret+Rel Fan | Exhaust Fan | [9 empty] | (ft2) |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW)
|  |  |  | (cfm) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | [5 empty] | Core_bottom Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 10586.7 | 1 | 7965.5 | 7965.5 | 0 | 0.592 | 0 | 0 | 9.351 | 0 | 2.577 | 0 | 11.928 | 0 | 3.235 | 3.235
BaseAirSys5 |  |  |  | 14224.8 | 20.1411 | 0 | 0.78392 | 0 | 0.21608 | 0 | 18.4922 | 24.26 | 19.0179 | 0 | 5.242 | 5.242 | 0 | [5 empty] | Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 2231.8 | 1 | 2068 | 2068 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.84 | 0.84
BaseAirSys5-2 |  |  |  | 14266.4 | 21.191 | 0.825 | 0.75103 | 0.047473 | 0.16257 | 0.038932 | 18.5463 | 22.9193 | 17.213 | 1.088 | 3.726 | 4.814 | 0.89229 | [5 empty] | Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 1412.9 | 1 | 1330.9 | 1330.9 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.54 | 0.54
BaseAirSys5-3 |  |  |  | 14697.7 | 5.702 | 0.366 | 0.93581 | 0 | 0 | 0.064188 | 19.107 | 19.107 | 17.8806 | 0 | 0 | 0 | 1.2264 | [5 empty] | Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 2231.8 | 1 | 1431.7 | 1431.7 | 0 | 0.125 | 0 | 0 | 1.971 | 0 | 0.543 | 0 | 2.515 | 0 | 0.581 | 0.581
[23 empty] | Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 1412.8 | 1 | 1428.6 | 1428.6 | 0 | 0.079 | 0 | 0 | 1.248 | 0 | 0.344 | 0 | 1.592 | 0 | 0.58 | 0.58
[23 empty] | FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | Core_mid Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 10586.7 | 1 | 7360.4 | 7360.4 | 0 | 0.744 | 0 | 0 | 9.351 | 0 | 2.563 | 0 | 11.913 | 0 | 2.141 | 2.141
[23 empty] | Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 2231.8 | 1 | 2373.9 | 2373.9 | 500 | 0.612 | 0 | 0.556 | 2.048 | 0.616 | 0 | 0.458 | 3.122 | 0.127 | 0.691 | 0.818
[23 empty] | Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 1412.9 | 1 | 1492 | 1492 | 400 | 0.099 | 0 | 0.444 | 1.248 | 0 | 0.342 | 0.366 | 1.956 | 0.102 | 0.434 | 0.536
[23 empty] | Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 2231.8 | 1 | 1415.9 | 1415.9 | 0 | 0.157 | 0 | 0 | 1.971 | 0 | 0.54 | 0 | 2.511 | 0 | 0.412 | 0.412
[23 empty] | Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 1412.8 | 1 | 1624.1 | 1624.1 | 0 | 0.388 | 0 | 0 | 1.297 | 0.39 | 0 | 0 | 1.687 | 0 | 0.473 | 0.473
[23 empty] | MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | Core_top Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 10586.7 | 1 | 7618.8 | 7618.8 | 0 | 1 | 0.744 | 0 | 2.156 | 0 | 0 | 0 | 2.156 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_1 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 2231.8 | 1 | 2411.7 | 2411.7 | 245 | 1 | 0 | 0.613 | 0.7 | 0 | 0 | 0.224 | 0.924 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_2 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 1412.9 | 1 | 1474.9 | 1474.9 | 155 | 1 | 0 | 0.388 | 0.7 | 0 | 0 | 0.142 | 0.842 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_3 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 2231.8 | 1 | 1496.7 | 1496.7 | 0 | 1 | 0.157 | 0 | 0.933 | 0 | 0 | 0 | 0.933 | 0 | 0 | 0
[23 empty] | Perimeter_top_ZN_4 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 1412.8 | 1 | 1695.5 | 1695.5 | 0 | 1 | 0.099 | 0 | 0.847 | 0 | 0 | 0 | 0.847 | 0 | 0 | 0
[23 empty] | TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Fan Static Pressure Adj
Key:
Input Values
Intermediate Values
Check Values
Error
Tolerrance: | 1%
| PROPOSED | [29 empty] | Paste ap - FanPowerAdjustment -> | AirSystems
| Air Systems | [32 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
| System Name | Type | SupFanCap | RetFanCap | ReliefFanCap | ExhFanCap | SupFanPwr | RetFanPwr | ReliefFanPwr | ExhFanPwr | TotSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio |  |  | TotSysFanPwrAdj | FullyDuctedExhFanPwrAdj | ExhFiltersPDAdj | BiosftyCabPDAdj | FullyDuctedRetPDAdj | MERVGTE16PDAdj | GasPhaseAirCleanersPDAdj | FullyDuctedExhDevFlow | ExhFiltersDevFlow | BiosftyCabDevFlow | FullyDuctedRetDevFlow | MERVGTE16DevFlow | GasPhaseAirCleanersDevFlow |  | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj | Fully Ducted Exhaust Pressure Drop Adj | Exhaust Filter Pressure Drop Adj | Biosafety Cabinet Pressure Drop Adj | Fully Ducted Return Pressure Drop Adj | MERV16 Filter Pressure Drop Adj | Air Cleaner Pressure Drop Adj | Fully Ducted Exhaust Design Flow | Exhaust Filter Design Flow | Biosafety Design Flow | Fully Ducted Return Design Flow | MERV16 Filter Design Flow | Air Cleaner Design Flow
|  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) |  |  | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
| BottomVAV | PVAV | 17875.9 | 16982.1 | 0 | 0 | 18.512 | 6.695 | 0 | 0 | 25.207 | 0.734 | 0.266 | 0 | 0 |  |  | 7.2482 | 0 | 0 | 0 | 0.5 | 1.2 | 0 | 0 | 0 | 0 | 16982 | 17876 | 0 |  | BottomVAV | PVAV | 17875.9 | 16982.1 | 0 | 0 | 18.512 | 6.695 | 0 | 0 | 25.207 | 0.734 | 0.266 | 0 | 0 | 0 | 7.259 | 7.259 | 0 | 0 | 0 | 0.5 | 1.2 | 0 | 0 | 0 | 0 | 16982 | 17876 | 0
| Mid VAV-SW Zones | PVAV | 4373.5 | 3691.2 | 0 | 0 | 3.092 | 1.157 | 0 | 0 | 4.249 | 0.728 | 0.272 | 0 | 0 |  |  | 1.2703 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 4373 | 0 |  | Mid VAV-SW Zones | PVAV | 4373.5 | 3691.2 | 0 | 0 | 3.092 | 1.157 | 0 | 0 | 4.249 | 0.728 | 0.272 | 0 | 0 | 0 | 1.272 | 1.272 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 4373 | 0
| Mid VAV NE_Core Zones | PVAV | 14231.4 | 0 | 13519.8 | 0 | 11.137 | 0 | 3.55 | 0 | 14.687 | 0.758 | 0 | 0.242 | 0 |  |  | 3.4449 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 14231 |  | Mid VAV NE_Core Zones | PVAV | 14231.4 | 0 | 13519.8 | 0 | 11.137 | 0 | 3.55 | 0 | 14.687 | 0.758 | 0 | 0.242 | 0 | 0 | 3.45 | 3.45 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 14231
| Mid SE Zones ExhSys | Exhaust | 0 | 0 | 0 | 2619.4 | 0 | 0 | 0 | 2.116 | 2.116 | 0 | 0 | 0 | 1 |  |  | 0.95098 | 0.5 | 0 | 1 | 0 | 0 | 0 | 2619 | 0 | 2619 | 0 | 0 | 0 |  | Mid SE Zones ExhSys | Exhaust | 0 | 0 | 0 | 2619.4 | 0 | 0 | 0 | 2.116 | 2.116 | 0 | 0 | 0 | 1 | 0.953 | 0 | 0.953 | 0.5 | 0 | 1 | 0 | 0 | 0 | 2619 | 0 | 2619 | 0 | 0 | 0
| TopFlrDOAS | DOASCV | 2134.7 | 0 | 0 | 0 | 1.561 | 0 | 0 | 0 | 1.561 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | TopFlrDOAS | DOASCV | 2134.7 | 0 | 0 | 0 | 1.561 | 0 | 0 | 0 | 1.561 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Restroom ExhSys | Exhaust | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0.211 | 0.211 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Restroom ExhSys | Exhaust | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0.211 | 0.211 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ZoneSystems
| Zone Systems | [32 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
| System Name | Type | SupFanCap | RetFanCap | ReliefFanCap | ExhFanCap | SupFanPwr | RetFanPwr | ReliefFanPwr | ExhFanPwr | TotSysFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio |  |  | TotSysFanPwrAdj | FullyDuctedExhPDAdj | ExhFiltersPDAdj | BiosftyCabPDAdj | FullyDuctedRetPDAdj | MERVGTE16PDAdj | GasPhaseAirCleanersPDAdj | FullyDuctedExhDevFlow | ExhFiltersDevFlow | BiosftyCabDevFlow | FullyDuctedRetDevFlow | MERVGTE16DevFlow | GasPhaseAirCleanersDevFlow |  | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj | Fully Ducted Exhaust Pressure Drop Adj | Exhaust Filter Pressure Drop Adj | Biosafety Cabinet Pressure Drop Adj | Fully Ducted Return Pressure Drop Adj | MERV16 Filter Pressure Drop Adj | Air Cleaner Pressure Drop Adj | Fully Ducted Exhaust Design Flow | Exhaust Filter Design Flow | Biosafety Design Flow | Fully Ducted Return Design Flow | MERV16 Filter Design Flow | Air Cleaner Design Flow
|  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) |  |  | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
| Perim_TopZn1_PTAC | PTAC | 2231.8 | 0 | 0 | 0 | 0.781 | 0 | 0 | 0 | 0.781 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn1_PTAC | PTAC | 2231.8 | 0 | 0 | 0 | 0.781 | 0 | 0 | 0 | 0.781 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perim_TopZn2_PTAC | PTAC | 1412.9 | 0 | 0 | 0 | 0.495 | 0 | 0 | 0 | 0.495 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn2_PTAC | PTAC | 1412.9 | 0 | 0 | 0 | 0.495 | 0 | 0 | 0 | 0.495 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perim_TopZn3_PTAC | PTAC | 2231.8 | 0 | 0 | 0 | 0.781 | 0 | 0 | 0 | 0.781 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn3_PTAC | PTAC | 2231.8 | 0 | 0 | 0 | 0.781 | 0 | 0 | 0 | 0.781 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Perim_TopZn4_PTAC | PTAC | 1412.8 | 0 | 0 | 0 | 0.494 | 0 | 0 | 0 | 0.494 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Perim_TopZn4_PTAC | PTAC | 1412.8 | 0 | 0 | 0 | 0.494 | 0 | 0 | 0 | 0.494 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Core_TopZn_PTAC | PTAC | 10586.7 | 0 | 0 | 0 | 3.705 | 0 | 0 | 0 | 3.705 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Core_TopZn_PTAC | PTAC | 10586.7 | 0 | 0 | 0 | 3.705 | 0 | 0 | 0 | 3.705 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CopyRoom ExhSys | Exhaust | 0 | 0 | 0 | 706.5 | 0 | 0 | 0 | 0.373 | 0.373 | 0 | 0 | 0 | 1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 706 | 0 | 0 | 0 | 0 | 0 | 0 |  | CopyRoom ExhSys | Exhaust | 0 | 0 | 0 | 706.5 | 0 | 0 | 0 | 0.373 | 0.373 | 0 | 0 | 0 | 1 | 0.171 | 0 | 0.171 | 1 | 0 | 0 | 0 | 0 | 706 | 0 | 0 | 0 | 0
Thermal Zone
[38 empty] | Fan Capacity |  |  | Fan Flow Ratio |  |  | Fan Pwr |  |  |  |  | Fan Pwr Adj
| Thermal Zone | PriAirCondgSysRef | VentSysRef | ExhSysRef | PriAirCondgSysDsgnFlow | VentSysDsgnFlow | DsgnExhFlow | PriZnToSysAirFlowRatio | VentZnToSysAirFlowRatio | ExhZnToSysAirFlowRatio | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | TotExhFanPwrAdj | TotNonExhFanPwrAdj | TotFanPwrAdj | FullyDuctedExhPDAdj | ExhFiltersPDAdjAdj | BiosftyCabPDAdjAdj | FullyDuctedRetPDAdjAdj | MERVGTE16PDAdjAdj | GasPhaseAirCleanersPDAdjAdj | TotExhFanPwrAdj | TotNonExhFanPwrAdj | [5 empty] | Name | Pri. HVAC Sys. | Vent. Sys. | Exhaust Sys. | Floor Area | Multiplier | Pri. System Flow | Ventilation System Flow | Exhaust Flow | Zn. Pri. Air Flow to Sys. Air Flow Ratio | Zn. Vent. to Sys. Air Flow Ratio | Zn. Exhaust to Sys. Air Flow Ratio | Prop. Supply Fan Pwr. | Prop. Return Fan Pwr. | Prop. Relief Fan Pwr. | Prop. Exhaust Fan Pwr. | Total Prop. Fan Pwr | Total Exhaust Fan Pwr. Adj | Total NonExhaust Fan Pwr. Adj | Total Fan Pwr. Adj | Fully Ducted Exhaust Pwr Adj | Exhaust Filter Fan Pwr Adj | Biosafety Cabinet Fan Pwr Adj | Fully Ducted Return Fan Pwr Adj | MERV16 Fan Pwr Adj | Air Cleaner Fan Pwr Adj | Exhaust Fan Motor BHP
[5 empty] | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp/cfm*1000) | (bhp/cfm*1000) | [9 empty] | (ft2) |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
| Core_bottom Thermal Zone | BottomVAV | BottomVAV | NONE | 10586.7 | 10586.7 | 0 | 0.59223 | 0 | 0 | 10.9634 | 3.965 | 0 | 0 | 14.9284 | 0 | 4.2926 | 4.2926 | 0 | 0 | 0 | 1.2173 | 3.0753 | 0 | 0 | 0.40547 | [5 empty] | Core_bottom Thermal Zone | BottomVAV | BottomVAV | NONE | 10586.7 | 1 | 10586.7 | 10586.7 | 0 | 0.592 | 0 | 0 | 10.963 | 3.965 | 0 | 0 | 14.928 | 0 | 4.299 | 4.299 | 0 | 0 | 0 | 1.219 | 3.08 | 0 | -99996
| Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 2231.8 | 0 | 0.12485 | 0 | 0 | 2.3112 | 0.83587 | 0 | 0 | 3.1471 | 0 | 0.90493 | 0.90493 | 0 | 0 | 0 | 0.25662 | 0.64831 | 0 | 0 | 0.40547 | [5 empty] | Perimeter_bot_ZN_1 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.125 | 0 | 0 | 2.311 | 0.836 | 0 | 0 | 3.147 | 0 | 0.906 | 0.906 | 0 | 0 | 0 | 0.257 | 0.649 | 0 | -99996
| Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.9 | 1412.9 | 0 | 0.079039 | 0 | 0 | 1.4632 | 0.52917 | 0 | 0 | 1.9923 | 0 | 0.57289 | 0.57289 | 0 | 0 | 0 | 0.16246 | 0.41043 | 0 | 0 | 0.40547 | [5 empty] | Perimeter_bot_ZN_2 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.9 | 1 | 1412.9 | 1412.9 | 0 | 0.079 | 0 | 0 | 1.463 | 0.529 | 0 | 0 | 1.992 | 0 | 0.574 | 0.574 | 0 | 0 | 0 | 0.163 | 0.411 | 0 | -99996
| Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 2231.8 | 0 | 0.12485 | 0 | 0 | 2.3112 | 0.83587 | 0 | 0 | 3.1471 | 0 | 0.90493 | 0.90493 | 0 | 0 | 0 | 0.25662 | 0.64831 | 0 | 0 | 0.40547 | [5 empty] | Perimeter_bot_ZN_3 Thermal Zone | BottomVAV | BottomVAV | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.125 | 0 | 0 | 2.311 | 0.836 | 0 | 0 | 3.147 | 0 | 0.906 | 0.906 | 0 | 0 | 0 | 0.257 | 0.649 | 0 | -99996
| Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.8 | 1412.8 | 0 | 0.079034 | 0 | 0 | 1.4631 | 0.52913 | 0 | 0 | 1.9922 | 0 | 0.57285 | 0.57285 | 0 | 0 | 0 | 0.16245 | 0.4104 | 0 | 0 | 0.40547 | [5 empty] | Perimeter_bot_ZN_4 Thermal Zone | BottomVAV | BottomVAV | NONE | 1412.8 | 1 | 1412.8 | 1412.8 | 0 | 0.079 | 0 | 0 | 1.463 | 0.529 | 0 | 0 | 1.992 | 0 | 0.574 | 0.574 | 0 | 0 | 0 | 0.163 | 0.411 | 0 | -99996
| FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 10586.7 | 10586.7 | 0 | 0.7439 | 0 | 0 | 8.2848 | 0 | 2.6408 | 0 | 10.9256 | 0 | 2.5627 | 2.5627 | 0 | 0 | 0 | 0 | 0 | 2.5627 | 0 | 0.24207 | [5 empty] | Core_mid Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 10586.7 | 1 | 10586.7 | 10586.7 | 0 | 0.744 | 0 | 0 | 8.285 | 0 | 2.641 | 0 | 10.925 | 0 | 2.567 | 2.567 | 0 | 0 | 0 | 0 | 0 | 2.567 | -99996
| Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2678.1 | 2678.1 | 500 | 0.61235 | 0 | 0.19088 | 1.8934 | 0.70849 | 0 | 0.40391 | 3.0058 | 0.18153 | 0.77786 | 0.95939 | 0.060509 | 0 | 0.12102 | 0 | 0.77786 | 0 | 0.36305 | 0.29045 | [5 empty] | Perimeter_mid_ZN_1 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | Mid SE Zones ExhSys | 2231.8 | 1 | 2678.1 | 2678.1 | 500 | 0.612 | 0 | 0.191 | 1.893 | 0.709 | 0 | 0.404 | 3.006 | 0.182 | 0.779 | 0.961 | 0.061 | 0 | 0.121 | 0 | 0.779 | 0 | -99996
| Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | Mid SE Zones ExhSys | 1412.9 | 0 | 2119.4 | 0.09928 | 0 | 0.80912 | 1.1057 | 0 | 0.35245 | 1.7121 | 3.1702 | 0.76945 | 0.34201 | 1.1115 | 0.25648 | 0 | 0.51297 | 0 | 0 | 0.34201 | 0.36305 | 0.24207 | [5 empty] | Perimeter_mid_ZN_2 Thermal Zone | Mid VAV NE_Core Zones | Mid SE Zones ExhSys | Mid SE Zones ExhSys | 1412.9 | 1 | 1412.9 | 0 | 2119.4 | 0.099 | 0 | 0.809 | 1.106 | 0 | 0.352 | 1.712 | 3.17 | 0.771 | 0.343 | 1.113 | 0.257 | 0 | 0.514 | 0 | 0 | 0.343 | -99996
| Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 2231.8 | 2231.8 | 0 | 0.15682 | 0 | 0 | 1.7465 | 0 | 0.55672 | 0 | 2.3032 | 0 | 0.54024 | 0.54024 | 0 | 0 | 0 | 0 | 0 | 0.54024 | 0 | 0.24207 | [5 empty] | Perimeter_mid_ZN_3 Thermal Zone | Mid VAV NE_Core Zones | Mid VAV NE_Core Zones | NONE | 2231.8 | 1 | 2231.8 | 2231.8 | 0 | 0.157 | 0 | 0 | 1.746 | 0 | 0.557 | 0 | 2.303 | 0 | 0.541 | 0.541 | 0 | 0 | 0 | 0 | 0 | 0.541 | -99996
| Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | NONE | 1695.4 | 1695.4 | 0 | 0.38765 | 0 | 0 | 1.1986 | 0.44851 | 0 | 0 | 1.6471 | 0 | 0.49243 | 0.49243 | 0 | 0 | 0 | 0 | 0.49243 | 0 | 0 | 0.29045 | [5 empty] | Perimeter_mid_ZN_4 Thermal Zone | Mid VAV-SW Zones | Mid VAV-SW Zones | NONE | 1412.8 | 1 | 1695.4 | 1695.4 | 0 | 0.388 | 0 | 0 | 1.198 | 0.449 | 0 | 0 | 1.647 | 0 | 0.493 | 0.493 | 0 | 0 | 0 | 0 | 0.493 | 0 | -99996
| MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS | NONE | 10586.7 | 1588 | 0 | 1 | 0.7439 | 0 | 4.8662 | 0 | 0 | 0 | 4.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Core_top Thermal Zone | Core_TopZn_PTAC | TopFlrDOAS | NONE | 10586.7 | 1 | 10586.7 | 1588 | 0 | 1 | 0.744 | 0 | 4.867 | 0 | 0 | 0 | 4.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Restroom ExhSys | Restroom ExhSys | 2231.8 | 0 | 400 | 1 | 0 | 1 | 0.781 | 0 | 0 | 0.211 | 0.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Perimeter_top_ZN_1 Thermal Zone | Perim_TopZn1_PTAC | Restroom ExhSys | Restroom ExhSys | 2231.8 | 1 | 2231.8 | 0 | 400 | 1 | 0 | 1 | 0.781 | 0 | 0 | 0.211 | 0.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | CopyRoom ExhSys | CopyRoom ExhSys | 1412.9 | 0 | 706.5 | 1 | 0 | 1 | 0.495 | 0 | 0 | 0.373 | 0.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Perimeter_top_ZN_2 Thermal Zone | Perim_TopZn2_PTAC | CopyRoom ExhSys | CopyRoom ExhSys | 1412.9 | 1 | 1412.9 | 0 | 706.5 | 1 | 0 | 1 | 0.495 | 0 | 0 | 0.373 | 0.868 | 0.171 | 0 | 0.171 | 0 | 0.171 | 0 | 0 | 0 | 0 | -99996
| Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS | NONE | 2231.8 | 334.8 | 0 | 1 | 0.15684 | 0 | 1.0258 | 0 | 0 | 0 | 1.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Perimeter_top_ZN_3 Thermal Zone | Perim_TopZn3_PTAC | TopFlrDOAS | NONE | 2231.8 | 1 | 2231.8 | 334.8 | 0 | 1 | 0.157 | 0 | 1.026 | 0 | 0 | 0 | 1.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS | NONE | 1412.8 | 211.9 | 0 | 1 | 0.099265 | 0 | 0.64895 | 0 | 0 | 0 | 0.64895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Perimeter_top_ZN_4 Thermal Zone | Perim_TopZn4_PTAC | TopFlrDOAS | NONE | 1412.8 | 1 | 1412.8 | 211.9 | 0 | 1 | 0.099 | 0 | 0.649 | 0 | 0 | 0 | 0.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BASELINE | [29 empty] | Paste ab - FanPowerAdjustment -> | AirSystems
| Air Systems | [32 empty] | Fan Capacity |  |  |  | Fan Pwr (Design) |  |  |  |  | Fan Pwr Ratio |  |  |  | Fan Pwr Adj
| System Name | Type | SupFanCap | RetFanCap | ReliefFanCap | ExhFanCap | TotPropSysFanPwr | PropExhFanPwr | SupFanPwrRatio | RetFanPwrRatio | ReliefFanPwrRatio | ExhFanPwrRatio | BaseFanBHPAllowance | BaseFanBHPAllowance | BaseFanBHPWithPressDropCredit | TotExhSysFanPwrAdj | TotNonExhSysFanPwrAdj | TotSysFanPwrAdj | Supply Fan | Return Fan | Relief Fan | Ret+Rel Fan | Exhaust Fan | Supply Fan | Exhaust Fan |  | Supply fan Check | Exhaust Fan Check |  |  |  | System Name | Type | Supply Fan Capacity | Return Fan Capacity | Relief Fan Capacity | Exhaust Fan Capacity | Supply Fan Pwr | Return Fan Pwr | Relief Fan Pwr | Exhaust Fan Pwr | Total System Fan Pwr | Supply Fan Pwr Ratio | Return Fan Pwr Ratio | Relief Fan Pwr Ratio | Exhaust Fan Pwr Ratio | Total Exhaust Fan Pwr Adj | Total NonExhaust Fan Pwr Adj | Total System Fan Pwr Adj | Fully Ducted Exhaust Pressure Drop Adj | Exhaust Filter Pressure Drop Adj | Biosafety Cabinet Pressure Drop Adj | Fully Ducted Return Pressure Drop Adj | MERV16 Filter Pressure Drop Adj | Air Cleaner Pressure Drop Adj | Fully Ducted Exhaust Design Flow | Exhaust Filter Design Flow | Biosafety Design Flow | Fully Ducted Return Design Flow | MERV16 Filter Design Flow | Air Cleaner Design Flow
|  |  | (cfm) |  |  |  | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp/cfm*1000) | (bhp) | (bhp) | (BHP) | (BHP) | (BHP) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp/cfm*1000) | (bhp/cfm*1000) | [8 empty] | (cfm) | (cfm) | (cfm) | (cfm) | (kW) | (kW) | (kW) | (kW) | (kW) | (frac.) | (frac.) | (frac.) | (frac.) | (bhp) | (bhp) | (bhp) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (in. w.c.) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
| BaseAirSys5 |  | 14228.5 | 0 | 0 | 0 | 25.2071 | 0 | 0.7344 | 0.2656 | 0 | 0 | 1.3 | 18.497 | 24.2663 | 0 | 5.7692 | 5.7692 | 24.2663 |  |  |  | 0 | 1.7055 | 0 |  |  | 0 |  |  |  | BaseAirSys5 | PVAV | 14228.5 | 0 | 0 | 0 | 19.337 | 0 | 0 | 0 | 25.207 | 0.734 | 0.266 | 0 | 0 | 0 | 5.778 | 5.778 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996
| BaseAirSys5-2 |  | 15562.6 | 0 | 0 | 2619.4 | 21.052 | 2.116 | 0.6759 | 0.054959 | 0.16863 | 0.10051 | 1.3 | 20.2314 | 25.2067 | 0.95098 | 4.0244 | 4.9754 | 22.6731 |  |  |  | 2.5336 | 1.4569 | 0.96725 |  |  | 2.5336 |  |  |  | BaseAirSys5-2 | PVAV | 15562.6 | 0 | 0 | 0 | 18.067 | 0 | 0 | 0 | 21.052 | 0.676 | 0.055 | 0.169 | 0.101 | 0.953 | 4.031 | 4.983 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996
| BaseAirSys5-3 |  | 14005.6 | 0 | 0 | 1106.5 | 8.401 | 0.584 | 0.93048 | 0 | 0 | 0.069516 | 1.3 | 18.2073 | 18.2073 | 0 | 0 | 0 | 16.9416 |  |  |  | 1.2657 | 1.2096 | 1.1439 |  |  | 1.2657 |  |  |  | BaseAirSys5-3 | PVAV | 14005.6 | 0 | 0 | 0 | 13.709 | 0 | 0 | 0 | 8.403 | 0.93 | 0 | 0 | 0.07 | 0.171 | 0 | 0.171 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996 | -99996
Thermal Zone
[38 empty] | Fan Capacity |  |  | Fan Flow Ratio |  |  | Fan Pwr |  |  |  |  | Fan Pwr Adj
| Thermal Zone | PriAirCondgSysRef |  |  | PriAirCondgSysDsgnFlow | VentSysDsgnFlow | DsgnExhFlow | TotPropSupFanPwr | TotPropRetFanPwr | TotPropReliefFanPwr | PropExhFanPwr | TotPropFanPwr | BaseToPropDsgnSupFlowRat | ZnToSysPropExhFanPwrRat | ZnToSysPropExhFanFlowRat | TotExhFanPwrAdj | TotNonExhFanPwrAdj | TotFanPwrAdj | FullyDuctedExhPwrAdj | ExhFiltersFanPwrAdj | BiosftyCabFanPwrAdj | FullyDuctedRetFanPwrAdj | MERVGTE16FanPwrAdj | GasPhaseAirCleanersFanPwrAdj | TotExhFanPwrAdj | TotNonExhFanPwrAdj | ExhFanMtrBHP |  |  |  |  | Name | Pri. HVAC Sys. | Vent. Sys. | Exhaust Sys. | Floor Area | Multiplier | Pri. System Flow | Ventilation System Flow | Exhaust Flow | Zn. Pri. Air Flow to Sys. Air Flow Ratio | Zn. Vent. to Sys. Air Flow Ratio | Zn. Exhaust to Sys. Air Flow Ratio | Prop. Supply Fan Pwr. | Prop. Return Fan Pwr. | Prop. Relief Fan Pwr. | Prop. Exhaust Fan Pwr. | Total Prop. Fan Pwr | Total Exhaust Fan Pwr. Adj | Total NonExhaust Fan Pwr. Adj | Total Fan Pwr. Adj | Fully Ducted Exhaust Pwr Adj | Exhaust Filter Fan Pwr Adj | Biosafety Cabinet Fan Pwr Adj | Fully Ducted Return Fan Pwr Adj | MERV16 Fan Pwr Adj | Air Cleaner Fan Pwr Adj | Exhaust Fan Motor BHP
[5 empty] | (cfm) |  |  | (kW) | (kW) | (kW) | (kW) | (kW) | (frac) | (frac) | (frac) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp/cfm*1000) | (bhp/cfm*1000) | (bhp) | W/cfm | [7 empty] | (ft2) |  | (cfm) | (cfm) | (cfm) | (frac.) | (frac.) | (frac.) | (kW) | (kW) | (kW) | (kW) | (kW) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp) | (bhp)
| Core_bottom Thermal Zone | BaseAirSys5 |  |  | 7965.2 | 7965.2 | 0 | 10.9634 | 3.965 | 0 | 0 | 14.9284 | 0.75238 | 0 | 0 | 0 | 3.2297 | 3.2297 | 0 | 0 | 0 | 0.91587 | 2.3138 | 0 | 0 | 0.40547 | 0 |  |  |  |  | Core_bottom Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 10586.7 | 1 | 7965.2 | 7965.2 | 0 | 0.592 | 0 | 0 | 10.963 | 3.965 | 0 | 0 | 14.928 | 0 | 3.235 | 3.235 | 0 | 0 | 0 | 0.917 | 2.317 | 0 | -99996
| Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys5 |  |  | 2069.4 | 2069.4 | 0 | 2.3112 | 0.83587 | 0 | 0 | 3.1471 | 0.92723 | 0 | 0 | 0 | 0.83908 | 0.83908 | 0 | 0 | 0 | 0.23795 | 0.60114 | 0 | 0 | 0.40547 | 0 |  |  |  |  | Perimeter_bot_ZN_1 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 2231.8 | 1 | 2069.4 | 2069.4 | 0 | 0.125 | 0 | 0 | 2.311 | 0.836 | 0 | 0 | 3.147 | 0 | 0.84 | 0.84 | 0 | 0 | 0 | 0.238 | 0.602 | 0 | -99996
| Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys5 |  |  | 1332.1 | 1332.1 | 0 | 1.4632 | 0.52917 | 0 | 0 | 1.9923 | 0.94281 | 0 | 0 | 0 | 0.54013 | 0.54013 | 0 | 0 | 0 | 0.15317 | 0.38696 | 0 | 0 | 0.40547 | 0 |  |  |  |  | Perimeter_bot_ZN_2 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 1412.9 | 1 | 1332.1 | 1332.1 | 0 | 0.079 | 0 | 0 | 1.463 | 0.529 | 0 | 0 | 1.992 | 0 | 0.541 | 0.541 | 0 | 0 | 0 | 0.153 | 0.388 | 0 | -99996
| Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys5 |  |  | 1431.9 | 1431.9 | 0 | 2.3112 | 0.83587 | 0 | 0 | 3.1471 | 0.64159 | 0 | 0 | 0 | 0.58059 | 0.58059 | 0 | 0 | 0 | 0.16464 | 0.41595 | 0 | 0 | 0.40547 | 0 |  |  |  |  | Perimeter_bot_ZN_3 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 2231.8 | 1 | 1431.9 | 1431.9 | 0 | 0.125 | 0 | 0 | 2.311 | 0.836 | 0 | 0 | 3.147 | 0 | 0.582 | 0.582 | 0 | 0 | 0 | 0.165 | 0.417 | 0 | -99996
| Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys5 |  |  | 1429.8 | 1429.8 | 0 | 1.4631 | 0.52913 | 0 | 0 | 1.9922 | 1.012 | 0 | 0 | 0 | 0.57974 | 0.57974 | 0 | 0 | 0 | 0.1644 | 0.41534 | 0 | 0 | 0.40547 | 0 |  |  |  |  | Perimeter_bot_ZN_4 Thermal Zone | BaseAirSys5 | BaseAirSys5 | NONE | 1412.8 | 1 | 1429.8 | 1429.8 | 0 | 0.079 | 0 | 0 | 1.463 | 0.529 | 0 | 0 | 1.992 | 0 | 0.581 | 0.581 | 0 | 0 | 0 | 0.165 | 0.416 | 0 | -99996
| FirstFloor_Plenum Thermal Zone | NONE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FirstFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Core_mid Thermal Zone | BaseAirSys5-2 |  |  | 7621.7 | 7621.7 | 0 | 8.2848 | 0 | 2.6408 | 0 | 10.9256 | 0.71993 | 0 | 0 | 0 | 1.8449 | 1.8449 | 0 | 0 | 0 | 0 | 0 | 1.8449 | 0 | 0.24207 | 0 |  |  |  |  | Core_mid Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 10586.7 | 1 | 7621.7 | 7621.7 | 0 | 0.744 | 0 | 0 | 8.285 | 0 | 2.641 | 0 | 10.925 | 0 | 1.848 | 1.848 | 0 | 0 | 0 | 0 | 0 | 1.848 | -99996
| Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys5-2 |  |  | 3657.7 | 3657.7 | 500 | 1.8934 | 0.70849 | 0 | 0.40391 | 3.0058 | 1.3658 | 0.19088 | 1 | 0.18153 | 1.0624 | 1.2439 | 0.060509 | 0 | 0.12102 | 0 | 1.0624 | 0 | 0.36305 | 0.29045 | 0.48362 |  |  |  |  | Perimeter_mid_ZN_1 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 2231.8 | 1 | 3657.7 | 3657.7 | 500 | 0.612 | 0 | 0.191 | 1.893 | 0.709 | 0 | 0.404 | 3.006 | 0.182 | 1.064 | 1.246 | 0.061 | 0 | 0.121 | 0 | 1.064 | 0 | 0.484
| Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys5-2 |  |  | 1182.6 | 0 | 2119.4 | 1.1057 | 0 | 0.35245 | 1.7121 | 3.1702 | 0.837 | 0.80912 | 1 | 0.76945 | 0.28627 | 1.0557 | 0.25648 | 0 | 0.51297 | 0 | 0 | 0.28627 | 0.36305 | 0.24207 | 2.05 |  |  |  |  | Perimeter_mid_ZN_2 Thermal Zone | BaseAirSys5-2 | NONE | NONE | 1412.9 | 1 | 1182.6 | 0 | 2119.4 | 0.099 | 0 | 0.809 | 1.106 | 0 | 0.352 | 1.712 | 3.17 | 0.771 | 0.287 | 1.057 | 0.257 | 0 | 0.514 | 0 | 0 | 0.287 | 2.051
| Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys5-2 |  |  | 1442.2 | 1442.2 | 0 | 1.7465 | 0 | 0.55672 | 0 | 2.3032 | 0.6462 | 0 | 0 | 0 | 0.34911 | 0.34911 | 0 | 0 | 0 | 0 | 0 | 0.34911 | 0 | 0.24207 | 0 |  |  |  |  | Perimeter_mid_ZN_3 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 2231.8 | 1 | 1442.2 | 1442.2 | 0 | 0.157 | 0 | 0 | 1.746 | 0 | 0.557 | 0 | 2.303 | 0 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0.35 | -99996
| Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys5-2 |  |  | 1658.3 | 1658.3 | 0 | 1.1986 | 0.44851 | 0 | 0 | 1.6471 | 0.97812 | 0 | 0 | 0 | 0.48166 | 0.48166 | 0 | 0 | 0 | 0 | 0.48166 | 0 | 0 | 0.29045 | 0 |  |  |  |  | Perimeter_mid_ZN_4 Thermal Zone | BaseAirSys5-2 | BaseAirSys5-2 | NONE | 1412.8 | 1 | 1658.3 | 1658.3 | 0 | 0.388 | 0 | 0 | 1.198 | 0.449 | 0 | 0 | 1.647 | 0 | 0.482 | 0.482 | 0 | 0 | 0 | 0 | 0.482 | 0 | -99996
| MidFloor_Plenum Thermal Zone | NONE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | MidFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Core_top Thermal Zone | BaseAirSys5-3 |  |  | 7524.2 | 7524.2 | 0 | 4.8662 | 0 | 0 | 0 | 4.8662 | 0.71072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Core_top Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 10586.7 | 1 | 7524.2 | 7524.2 | 0 | 1 | 0.744 | 0 | 4.867 | 0 | 0 | 0 | 4.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Perimeter_top_ZN_1 Thermal Zone | BaseAirSys5-3 |  |  | 1951 | 0 | 400 | 0.781 | 0 | 0 | 0.211 | 0.992 | 0.87418 | 0.3613 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4573 |  |  |  |  | Perimeter_top_ZN_1 Thermal Zone | BaseAirSys5-3 | NONE | NONE | 2231.8 | 1 | 1951 | 0 | 400 | 1 | 0 | 1 | 0.781 | 0 | 0 | 0.211 | 0.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.462
| Perimeter_top_ZN_2 Thermal Zone | BaseAirSys5-3 |  |  | 1353.5 | 0 | 706.5 | 0.495 | 0 | 0 | 0.373 | 0.868 | 0.95796 | 0.6387 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80839 |  |  |  |  | Perimeter_top_ZN_2 Thermal Zone | BaseAirSys5-3 | NONE | NONE | 1412.9 | 1 | 1353.5 | 0 | 706.5 | 1 | 0 | 1 | 0.495 | 0 | 0 | 0.373 | 0.868 | 0.171 | 0 | 0.171 | 0 | 0.171 | 0 | 0 | 0 | 0 | 0.817
| Perimeter_top_ZN_3 Thermal Zone | BaseAirSys5-3 |  |  | 1489.5 | 1489.5 | 0 | 1.0258 | 0 | 0 | 0 | 1.0258 | 0.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Perimeter_top_ZN_3 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 2231.8 | 1 | 1489.5 | 1489.5 | 0 | 1 | 0.157 | 0 | 1.026 | 0 | 0 | 0 | 1.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| Perimeter_top_ZN_4 Thermal Zone | BaseAirSys5-3 |  |  | 1687.4 | 1687.4 | 0 | 0.64895 | 0 | 0 | 0 | 0.64895 | 1.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Perimeter_top_ZN_4 Thermal Zone | BaseAirSys5-3 | BaseAirSys5-3 | NONE | 1412.8 | 1 | 1687.4 | 1687.4 | 0 | 1 | 0.099 | 0 | 0.649 | 0 | 0 | 0 | 0.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| TopFloor_Plenum Thermal Zone | NONE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | TopFloor_Plenum Thermal Zone | NONE | NONE | NONE | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99996
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Single-zone
|  |  | Lab, BldgExhFlow < 10,000cfm, no exh filters |  |  |  |  | Lab, BldgExhFlow > 10,000cfm, no exh filters
[5 empty] | BHPAllow | 0.94 | bhp/1000cfm |  |  | BHPAllow | 1.3 | bhp/1000cfm
[5 empty] | BHP | 5.1719 |  |  |  | BHP | 7.1526
[5 empty] | BHPAdj | 0 | hp |  |  | BHPAdj | 0 | hp
[5 empty] | BHPAllow+Adj | 5.1719 | hp |  |  | BHPAllow+Adj | 7.1526 | hp
|  |  | Proposed |  |  | Standard |  | Proposed |  |  | Standard
| Mult | [6 empty] | 2 |  |  | 2
| SupFanCap |  | 5502 | 0.5 |  | 5502 |  | 5502 | 0.5 |  | 5502
| ExhFanCap |  | 5502 | 0.5 |  | 5502 |  | 5502 | 0.5 |  | 5502
| SupFanPwr |  | 2.751 | 0.5 |  | 2.5859 | hp | 2.751 | 0.5 |  | 3.5763 | hp
| ExhFanPwr |  | 2.751 | 0.5 |  | 2.5859 | hp | 2.751 | 0.5 |  | 3.5763 | hp
[6 empty] | 5.1719 | hp |  |  |  | 7.1526 | hp
[6 empty] | 5502 |  |  |  |  | 5502
Supply | MtrEff |  |  |  |  | 0.895 |  |  |  |  | 0.917
| TotEff |  |  |  |  | 0.58175 |  |  |  |  | 0.59605
| TotStaticPress |  |  |  |  | 1.9386 |  |  |  |  | 5.362
| SupFanPwr |  |  |  |  | 2154.2758 |  |  |  |  | 5815.6752
| FanPwrIdx |  |  |  |  | 0.39154 |  |  |  |  | 1.057
| MtrBHP |  |  |  |  | 2.5859 |  |  |  |  | 7.1526
Exhaust | ExhFlow | cfm | 5502 |  |  | 5502 |  | 5502 |  |  | 5502
| ExhFanMtrEff |  |  |  |  | 0.895 |  |  |  |  | 0.895
| ExhTotEff |  | 0.56225 |  |  | 0.5549 |  | 0.56225 |  |  | 0.5549
| ExhTotStaticPress | inH2O | 2.7754 |  |  | 1.8491 |  | 2.7754 |  |  | 3.0697
| ExhFanPwr |  | 3191.158 |  |  | 2154.2782 |  | 3191.158 |  |  | 3576.3005
| ExhFanPwrIdx |  | 0.58 |  |  | 0.39154 |  | 0.58 |  |  | 0.65
| ExhFanMtrBHP |  |  |  |  | 2.5859 |  |  |  |  | 4.2929
[6 empty] | 5.1719 |  |  |  |  | 11.4455